## Section III (Method A.1)
Test Procedure for Bare Pumps - Calculation Method (A.1) Section III of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps -----------------------------------------------------------------------------------------------Test Procedure for Bare Pumps - Calculation Method (A.1) Section III of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps----------------------------------------------------------------------------------Test Procedure for Bare Pumps - Calculation Method (A.1) Section III of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps | [61 empty] | Not part of Calculation Method (A.1) Section III of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps
Initial Database Entry Fields for all Basic Model Listings (Entered by User) | [19 empty] | Universal Lookups & Calculations | [7 empty] | Pump Energy Rating Standard Calculation | [19 empty] | Pump Energy Index Calculation | [13 empty] | HI Energy Rating Calculation for HI 40.5 Energy Rating Program
[5 empty] | nsp |  |  |  | S | Q100% | H100% | P100% | Q75% | H75% | P75% | Q110% | H110% | P110% | P120% |  | PMotRated | Ns | MotorHP |  | ηmotor,full | Lfull | C | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | X100% | X75% | X110% | Y100% | Y75% | Y110% | L100% | L75% | L110% | P100%in,M | P75%in,M | P110%in,M | PERCL | PEICL | CBaseline | ƞpump,Baseline | Pu,100% | Pu,75% | Pu,110% | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | Rating Load Type | Configuration for which the pump is being rated | DOE Pump Category | If ST - Enter Bowl Diameter (in) | Nominal Speed of rotation | Basic Model Designation | Basic Model Full Impeller Diameter (in) | If applicable - HI Approved Laboratory Registration Number | Number of Stages Tested | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 100% of BEP Rate of Flow (hp) | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 75% of BEP Rate of Flow (hp) | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 110% of BEP Rate of Flow (hp) | Pump Power Input at 120% of BEP Rate of Flow (hp) | DOE Equipment Category | Power for selection of default motor | Calculate Specific Speed | Rated Motor Power used for default losses or Nameplate Rated Motor Power | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Lookup Standard C-Value | Calculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Calculate Pump Energy Rating Standard | Calculate pump power input to motor power ratio 100% BEP | Calculate pump power input to motor power ratio 75% BEP | Calculate pump power input to motor power ratio 110% BEP | Calculate Part load loss factor at 100% BEP | Calculate Part load loss factor at 75% BEP | Calculate Part load loss factor at 110% BEP | Calculate part load loss at 100% BEP | Calculate part load loss at 75% BEP | Calculate part load loss at 110% BEP | Calculate driver power input at 100% BEP | Calculate driver power input at 75% BEP | Calculate driver power input at 110% BEP | Calculate Pump Energy Rating Constant Load | Calculate Pump Energy Index Constant Load | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
#REF! | #REF! | #REF! | ST | 4 | 3600 | #REF! | #REF! | #REF! | 8 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | 53 | ST-3600 | 46.087 | 3425.2672 | 50 | ST-50-3600 | 80 | 12.5 | 134.85 | 69.4528 | 37.5325 | 33.0878 | 37.302 | 54.0403 | 50.307 | 54.5263 | 1 | 1 | 1 | 1 | 1 | 1 | 12.5 | 12.5 | 12.5 | 66.5403 | 62.807 | 67.0263 | 65.4513 | 1 | 0.98403 | 1 | 1 | 0.98883 | 1 | 12.5 | 12.3604 | 12.5 | 63.9144 | 61.5617 | 64.3084 | 63.2551 | 0.96645 | 138.78 | 65.5228 | 37.5325 | 33.0878 | 37.302 | 57.2816 | 53.3244 | 57.7968 | 1 | 1 | 1 | 1 | 1 | 1 | 12.5 | 12.5 | 12.5 | 69.7816 | 65.8244 | 70.2968 | 68.6274 | 1.0485 | 8.208
#REF! | #REF! | #REF! | RSV | 4 | 3600 | #REF! | #REF! | #REF! | 2 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | 53 | RSV-3600 | 53 | 1211.0148 | 60 | RSV-60-3600 | 93.6 | 4.1026 | 133.2 | 68.3577 | 37.5325 | 33.0878 | 37.302 | 54.906 | 51.113 | 55.3999 | 0.9151 | 0.85188 | 0.92333 | 0.94026 | 0.89571 | 0.94608 | 3.8575 | 3.6747 | 3.8814 | 58.7635 | 54.7877 | 59.2812 | 57.605 | 0.85691 | 0.82002 | 0.86347 | 0.89924 | 0.87348 | 0.90385 | 3.6892 | 3.5835 | 3.7081 | 55.1035 | 52.7848 | 55.5165 | 54.4628 | 0.94545 | 133.2 | 68.3577 | 37.5325 | 33.0878 | 37.302 | 54.906 | 51.113 | 55.3999 | 0.9151 | 0.85188 | 0.85188 | 0.94026 | 0.89571 | 0.89571 | 3.8575 | 3.6747 | 3.6747 | 58.7635 | 54.7877 | 59.0746 | 57.5362 | 0.9988 | 5.3352
#REF! | #REF! | #REF! | ESCC | 4 | 3600 | #REF! | #REF! | #REF! | 1 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | 53 | ESCC-3600 | 53 | 720.0737 | 60 | ESCC-60-3600 | 93.6 | 4.1026 | 130.42 | 60.4576 | 37.5325 | 33.0878 | 37.302 | 62.0807 | 57.792 | 62.6391 | 1 | 0.9632 | 1 | 1 | 0.97421 | 1 | 4.1026 | 3.9968 | 4.1026 | 66.1833 | 61.7888 | 66.7416 | 64.8981 | 0.85691 | 0.82002 | 0.86347 | 0.89924 | 0.87348 | 0.90385 | 3.6892 | 3.5835 | 3.7081 | 55.1035 | 52.7848 | 55.5165 | 54.4628 | 0.83921 | 135.94 | 54.9376 | 37.5325 | 33.0878 | 37.302 | 68.3184 | 63.5988 | 68.9329 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1026 | 4.1026 | 4.1026 | 72.421 | 67.7014 | 73.0355 | 71.0455 | 1.0947 | 25.5519
#REF! | #REF! | #REF! | IL | 4 | 3600 | #REF! | #REF! | #REF! | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | 53 | IL-3600 | 53 | 1641.4132 | 60 | IL-60-3600 | 93.6 | 4.1026 | 133.84 | 71.0887 | 37.5325 | 33.0878 | 37.302 | 52.7967 | 49.1494 | 53.2716 | 0.87995 | 0.81916 | 0.88786 | 0.91544 | 0.87288 | 0.92103 | 3.7557 | 3.5811 | 3.7786 | 56.5524 | 52.7304 | 57.0502 | 55.4388 | 0.85691 | 0.82002 | 0.86347 | 0.89924 | 0.87348 | 0.90385 | 3.6892 | 3.5835 | 3.7081 | 55.1035 | 52.7848 | 55.5165 | 54.4628 | 0.9824 | 141.01 | 63.9187 | 37.5325 | 33.0878 | 37.302 | 58.7191 | 54.6627 | 59.2473 | 0.97865 | 0.91104 | 0.91104 | 0.98507 | 0.9374 | 0.9374 | 4.0413 | 3.8457 | 3.8457 | 62.7604 | 58.5084 | 63.093 | 61.4478 | 1.1084 | 12.5994
#REF! | #REF! | #REF! | ESFM | 1 | 3600 | #REF! | #REF! | #REF! | 4 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | 53 | ESFM-3600 | 53 | 2036.6761 | 60 | ESFM-60-3600 | 93.6 | 4.1026 | 130.99 | 75.0428 | 37.5325 | 33.0878 | 37.302 | 50.0148 | 46.5596 | 50.4646 | 0.83358 | 0.77599 | 0.84108 | 0.88292 | 0.84322 | 0.88815 | 3.6222 | 3.4594 | 3.6437 | 53.637 | 50.019 | 54.1083 | 52.5829 | 0.85691 | 0.82002 | 0.86347 | 0.89924 | 0.87348 | 0.90385 | 3.6892 | 3.5835 | 3.7081 | 55.1035 | 52.7848 | 55.5165 | 54.4628 | 1.0358 | 136.59 | 69.4428 | 37.5325 | 33.0878 | 37.302 | 54.0481 | 50.3143 | 54.5342 | 0.9008 | 0.83857 | 0.83857 | 0.93016 | 0.8864 | 0.8864 | 3.816 | 3.6365 | 3.6365 | 57.8641 | 53.9508 | 58.1707 | 56.6562 | 1.0775 | 4.1714
#REF! | #REF! | #REF! | ST | 4 | 1800 | #REF! | #REF! | #REF! | 8 | 349.8305 | 424.4298 | 27 | 262.3729 | 498.8911 | 29 | 384.8136 | 383.476 | 29.5 | 29.9 | ST-1800 | 26 | 1712.6336 | 30 | ST-30-1800 | 80 | 7.5 | 138.78 | 66.4505 | 37.5325 | 33.0878 | 37.302 | 56.4818 | 52.5799 | 56.9899 | 1 | 1 | 1 | 1 | 1 | 1 | 7.5 | 7.5 | 7.5 | 63.9818 | 60.0799 | 64.4899 | 62.8443 | 0.9 | 0.96667 | 0.98333 | 0.9296 | 0.97665 | 0.98835 | 6.972 | 7.3249 | 7.4126 | 33.972 | 36.3249 | 36.9126 | 35.7329 | 0.56859 | 138.78 | 66.4505 | 37.5325 | 33.0878 | 37.302 | 56.4818 | 52.5799 | 56.9899 | 1 | 1 | 1 | 1 | 1 | 1 | 7.5 | 7.5 | 7.5 | 63.9818 | 60.0799 | 64.4899 | 62.8443 | 1 | 43.1405
#REF! | #REF! | #REF! | RSV | 4 | 1800 | #REF! | #REF! | #REF! | 5 | 349.8305 | 424.4298 | 125 | 262.3729 | 498.8911 | 126.8 | 384.8136 | 383.476 | 130 | 131 | RSV-1800 | 131 | 1203.8558 | 150 | RSV-150-1800 | 95.8 | 6.5762 | 129.63 | 71.8409 | 37.5325 | 33.0878 | 37.302 | 52.2439 | 48.6348 | 52.7138 | 0.34829 | 0.32423 | 0.35143 | 0.62256 | 0.61653 | 0.62341 | 4.0941 | 4.0544 | 4.0997 | 56.338 | 52.6892 | 56.8135 | 55.2747 | 0.83333 | 0.84533 | 0.86667 | 0.88275 | 0.89113 | 0.9061 | 5.8051 | 5.8602 | 5.9587 | 130.8051 | 132.6602 | 135.9587 | 133.128 | 2.4085 | 129.63 | 71.8409 | 37.5325 | 33.0878 | 37.302 | 52.2439 | 48.6348 | 52.7138 | 0.34829 | 0.32423 | 0.32423 | 0.62256 | 0.61653 | 0.61653 | 4.0941 | 4.0544 | 4.0544 | 56.338 | 52.6892 | 56.7682 | 55.2596 | 0.99973 | -140.8753
#REF! | #REF! | #REF! | ESCC | 4 | 1800 | #REF! | #REF! | #REF! | 3 | 349.8305 | 424.4298 | 5.7 | 262.3729 | 498.8911 | 6.2 | 384.8136 | 383.476 | 6.7 | 6.8 | ESCC-1800 | 6.8 | 820.7066 | 7.5 | ESCC-7.5-1800 | 91 | 0.74176 | 128.47 | 65.6792 | 37.5325 | 33.0878 | 37.302 | 57.1451 | 53.1974 | 57.6591 | 1 | 1 | 1 | 1 | 1 | 1 | 0.74176 | 0.74176 | 0.74176 | 57.8869 | 53.9391 | 58.4009 | 56.7366 | 0.76 | 0.82667 | 0.89333 | 0.8324 | 0.8781 | 0.92489 | 0.61744 | 0.65134 | 0.68604 | 6.3174 | 6.8513 | 7.386 | 6.8509 | 0.12075 | 134.43 | 59.7192 | 37.5325 | 33.0878 | 37.302 | 62.8482 | 58.5065 | 63.4135 | 1 | 1 | 1 | 1 | 1 | 1 | 0.74176 | 0.74176 | 0.74176 | 63.59 | 59.2483 | 64.1553 | 62.3249 | 1.0985 | 97.7746
#REF! | #REF! | #REF! | IL | 1 | 1800 | #REF! | #REF! | #REF! | 4 | 349.8305 | 424.4298 | 76 | 262.3729 | 498.8911 | 75 | 384.8136 | 383.476 | 78 | 80 | IL-1800 | 80 | 1018.338 | 100 | IL-100-1800 | 95.4 | 4.8218 | 129.3 | 69.3871 | 37.5325 | 33.0878 | 37.302 | 54.0914 | 50.3547 | 54.578 | 0.54091 | 0.50355 | 0.54578 | 0.69979 | 0.68126 | 0.70231 | 3.3742 | 3.2849 | 3.3864 | 57.4657 | 53.6395 | 57.9643 | 56.3509 | 0.76 | 0.75 | 0.78 | 0.8324 | 0.82569 | 0.84595 | 4.0137 | 3.9813 | 4.079 | 80.0137 | 78.9813 | 82.079 | 80.35 | 1.4259 | 135.92 | 62.7671 | 37.5325 | 33.0878 | 37.302 | 59.7964 | 55.6655 | 60.3343 | 0.59796 | 0.55666 | 0.55666 | 0.73077 | 0.70803 | 0.70803 | 3.5236 | 3.414 | 3.414 | 63.32 | 59.0795 | 63.7482 | 62.0431 | 1.101 | -32.4873
#REF! | #REF! | #REF! | ESFM | 4 | 1800 | #REF! | #REF! | #REF! | 8 | 349.8305 | 424.4298 | 187 | 262.3729 | 498.8911 | 192 | 384.8136 | 383.476 | 193 | 196 | ESFM-1800 | 196 | 1712.6336 | 200 | ESFM-200-1800 | 95.8 | 8.7683 | 128.85 | 76.3805 | 37.5325 | 33.0878 | 37.302 | 49.1388 | 45.7442 | 49.5808 | 0.24569 | 0.22872 | 0.2479 | 0.60349 | 0.6021 | 0.60371 | 5.2915 | 5.2793 | 5.2935 | 54.4304 | 51.0235 | 54.8743 | 53.4374 | 0.935 | 0.96 | 0.965 | 0.95432 | 0.97196 | 0.97548 | 8.3678 | 8.5224 | 8.5532 | 195.3678 | 200.5224 | 201.5532 | 199.1279 | 3.7264 | 134.99 | 70.2405 | 37.5325 | 33.0878 | 37.302 | 53.4342 | 49.7429 | 53.9148 | 0.26717 | 0.24871 | 0.24871 | 0.606 | 0.60379 | 0.60379 | 5.3135 | 5.2942 | 5.2942 | 58.7478 | 55.0371 | 59.209 | 57.6589 | 1.079 | -264.738

## Section IV (Method B.2)
Testing-based approach for Pumps Sold with Motors - Calculation Method (B.2) Section IV of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps ---------------------------------------------------------------------Testing-based approach for Pumps Sold with Motors - Calculation Method (B.2) Section IV of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps | [52 empty] | Not part of Calculation Method (A.1) Section III of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps
Initial Database Entry Fields for all Basic Model Listings (Entered by User) | [24 empty] | Universal Lookups & Calculations | [5 empty] | Pump Energy Rating Standard Calculation | [19 empty] | Pump Energy Index Calculation |  | HI Energy Rating Calculation for HI 40.5 Energy Rating Program
[5 empty] | nsp |  |  |  |  | MotorHP,NP | ηmotor,full,NP | S | Q100% | H100% | P100%in,M | Q75% | H75% | P75%in,M | Q110% | H110% | P110%in,M |  |  |  |  | Ns |  | ηmotor,full | Lfull | C | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | PERCL | PEICL | CBaseline | ƞpump,Baseline | Pu,100% | Pu,75% | Pu,110% | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PEIBaseline | PERBaseline | ER
Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | Rating Load Type | Configuration for which the pump is being rated | DOE Pump Category | If ST - Enter Bowl Diameter (in) | Nominal Speed of rotation | Is motor regulated under 10CFR 431.25? | Basic Model Designation | Basic Model Full Impeller Diameter (in) | If applicable - HI Approved Laboratory Registration Number | Rated Motor Power used for default losses or Nameplate Rated Motor Power | If regulated under 10CFR 431.25 - Nameplate nominal motor efficiency | Number of Stages Tested | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Driver Power Input at 100% of BEP Rate of Flow (hp) | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Driver Power Input at 75% of BEP Rate of Flow (hp) | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Driver Power Input at 110% of BEP Rate of Flow (hp) | Basic Model Designation | Basic Model Full Impeller Diameter (in) | If applicable - HI Approved Laboratory Registration Number | DOE Equipment Category | Calculate Specific Speed | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Lookup Standard C-Value | Calculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Calculate Pump Energy Rating Standard | Calculate Pump Energy Rating Constant Load | Calculate Pump Energy Index Constant Load | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
#REF! | #REF! | #REF! | RSV | N/A | 3600 | No | xxx.xxx.xx | xxxxx | xxxx | 60 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-3600 | 3741.6129 | RSV-60-3600 | 93.6 | 4.1026 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.89119 | 0.82962 | 0.8992 | 0.92337 | 0.88016 | 0.92903 | 3.7882 | 3.6109 | 3.8114 | 57.2593 | 53.3881 | 57.7635 | 56.1314 | 50.8029 | 0.90507 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.89119 | 0.82962 | 0.8992 | 0.92337 | 0.88016 | 0.92903 | 3.7882 | 3.6109 | 3.8114 | 57.2593 | 53.3881 | 57.7635 | 56.1314 | 1 | 9.4928
#REF! | #REF! | #REF! | ST | N/A | 1800 | No | xxx.xxx.xx | xxxxx | xxxx | 50 | N/A | 5 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-1800 | 1203.8558 | ST-50-1800 | 82.5 | 10.6061 | 138.78 | 62.6909 | 37.5325 | 33.0878 | 37.302 | 59.8691 | 55.7332 | 60.4076 | 1 | 1 | 1 | 1 | 1 | 1 | 10.6061 | 10.6061 | 10.6061 | 70.4752 | 66.3393 | 71.0137 | 69.2691 | 50.8029 | 0.73341 | 138.78 | 62.6909 | 37.5325 | 33.0878 | 37.302 | 59.8691 | 55.7332 | 60.4076 | 1 | 1 | 1 | 1 | 1 | 1 | 10.6061 | 10.6061 | 10.6061 | 70.4752 | 66.3393 | 71.0137 | 69.2691 | 1 | 26.6587
#REF! | #REF! | #REF! | IL | N/A | 3600 | No | xxx.xxx.xx | xxxxx | xxxx | 25 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | IL-3600 | 1641.4132 | IL-25-3600 | 91.7 | 2.2628 | 133.84 | 71.0887 | 37.5325 | 33.0878 | 37.302 | 52.7967 | 49.1494 | 53.2716 | 1 | 1 | 1 | 1 | 1 | 1 | 2.2628 | 2.2628 | 2.2628 | 55.0595 | 51.4122 | 55.5344 | 53.9966 | 50.8029 | 0.94085 | 141.01 | 63.9187 | 37.5325 | 33.0878 | 37.302 | 58.7191 | 54.6627 | 59.2473 | 1 | 1 | 1 | 1 | 1 | 1 | 2.2628 | 2.2628 | 2.2628 | 60.9819 | 56.9255 | 61.5101 | 59.7998 | 1.1075 | 16.662
#REF! | #REF! | #REF! | ESCC | N/A | 1800 | Yes | xxx.xxx.xx | xxxxx | xxxx | 75 | 97 | 5 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ESCC-1800 | 1203.8558 | ESCC-75-1800 | 95 | 3.9474 | 128.47 | 73.0009 | 37.5325 | 33.0878 | 37.302 | 51.4137 | 47.862 | 51.8762 | 0.68552 | 0.63816 | 0.69168 | 0.78361 | 0.75432 | 0.78753 | 3.0932 | 2.9776 | 3.1087 | 54.5069 | 50.8395 | 54.9849 | 53.4384 | 50.8029 | 0.95068 | 134.43 | 67.0409 | 37.5325 | 33.0878 | 37.302 | 55.9845 | 52.1169 | 56.488 | 0.74646 | 0.69489 | 0.75317 | 0.82332 | 0.78958 | 0.82781 | 3.25 | 3.1168 | 3.2677 | 59.2344 | 55.2337 | 59.7557 | 58.0688 | 1.0866 | 13.5968
#REF! | #REF! | #REF! | ESFM | N/A | 1800 | No | xxx.xxx.xx | xxxxx | xxxx | 125 | N/A | 1 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ESFM-1800 | 360.0369 | ESFM-125-1800 | 95.4 | 6.0273 | 128.85 | 38.1351 | 37.5325 | 33.0878 | 37.302 | 98.4198 | 91.6207 | 99.305 | 0.78736 | 0.73297 | 0.79444 | 0.85097 | 0.81436 | 0.85582 | 5.129 | 4.9083 | 5.1583 | 103.5488 | 96.529 | 104.4633 | 101.5035 | 50.8029 | 0.5005 | 134.99 | 31.9951 | 37.5325 | 33.0878 | 37.302 | 117.3069 | 109.2031 | 118.3621 | 0.93846 | 0.87362 | 0.9469 | 0.95676 | 0.91099 | 0.96272 | 5.7667 | 5.4908 | 5.8026 | 123.0736 | 114.6939 | 124.1646 | 120.632 | 1.1885 | 68.7947
#REF! | #REF! | #REF! | RSV | N/A | 3600 | Yes | xxx.xxx.xx | xxxxx | xxxx | 50 | 95 | 5 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-3600 | 2407.7116 | RSV-50-3600 | 93 | 3.7634 | 133.2 | 72.9531 | 37.5325 | 33.0878 | 37.302 | 51.4474 | 47.8933 | 51.9102 | 1 | 0.95787 | 1 | 1 | 0.97045 | 1 | 3.7634 | 3.6522 | 3.7634 | 55.2109 | 51.5455 | 55.6736 | 54.1379 | 50.8029 | 0.9384 | 133.2 | 72.9531 | 37.5325 | 33.0878 | 37.302 | 51.4474 | 47.8933 | 51.9102 | 1 | 0.95787 | 1 | 1 | 0.97045 | 1 | 3.7634 | 3.6522 | 3.7634 | 55.2109 | 51.5455 | 55.6736 | 54.1379 | 1 | 6.1602
#REF! | #REF! | #REF! | RSV | N/A | 1800 | No | xxx.xxx.xx | xxxxx | xxxx | 75 | N/A | 4 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-1800 | 1018.338 | RSV-75-1800 | 95 | 3.9474 | 129.63 | 69.0571 | 37.5325 | 33.0878 | 37.302 | 54.3499 | 50.5953 | 54.8388 | 0.72467 | 0.6746 | 0.73118 | 0.80889 | 0.77672 | 0.81318 | 3.193 | 3.066 | 3.2099 | 57.5429 | 53.6613 | 58.0487 | 56.412 | 50.8029 | 0.90057 | 129.63 | 69.0571 | 37.5325 | 33.0878 | 37.302 | 54.3499 | 50.5953 | 54.8388 | 0.72467 | 0.6746 | 0.73118 | 0.80889 | 0.77672 | 0.81318 | 3.193 | 3.066 | 3.2099 | 57.5429 | 53.6613 | 58.0487 | 56.412 | 1 | 9.9431
#REF! | #REF! | #REF! | RSV | N/A | 3600 | No | xxx.xxx.xx | xxxxx | xxxx | 50 | N/A | 5 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-3600 | 2407.7116 | RSV-50-3600 | 93 | 3.7634 | 133.2 | 72.9531 | 37.5325 | 33.0878 | 37.302 | 51.4474 | 47.8933 | 51.9102 | 1 | 0.95787 | 1 | 1 | 0.97045 | 1 | 3.7634 | 3.6522 | 3.7634 | 55.2109 | 51.5455 | 55.6736 | 54.1379 | 50.8029 | 0.9384 | 133.2 | 72.9531 | 37.5325 | 33.0878 | 37.302 | 51.4474 | 47.8933 | 51.9102 | 1 | 0.95787 | 1 | 1 | 0.97045 | 1 | 3.7634 | 3.6522 | 3.7634 | 55.2109 | 51.5455 | 55.6736 | 54.1379 | 1 | 6.1602
#REF! | #REF! | #REF! | ESFM | N/A | 1800 | No | xxx.xxx.xx | xxxxx | xxxx | 50 | N/A | 5 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ESFM-1800 | 1203.8558 | ESFM-50-1800 | 94.5 | 2.9101 | 128.85 | 72.6209 | 37.5325 | 33.0878 | 37.302 | 51.6828 | 48.1124 | 52.1476 | 1 | 0.96225 | 1 | 1 | 0.97354 | 1 | 2.9101 | 2.8331 | 2.9101 | 54.5928 | 50.9455 | 55.0577 | 53.5266 | 50.8029 | 0.94911 | 134.99 | 66.4809 | 37.5325 | 33.0878 | 37.302 | 56.4561 | 52.5559 | 56.9639 | 1 | 1 | 1 | 1 | 1 | 1 | 2.9101 | 2.9101 | 2.9101 | 59.3661 | 55.466 | 59.8739 | 58.2295 | 1.0879 | 13.8746
#REF! | #REF! | #REF! | RSV | N/A | 3600 | No | xxx.xxx.xx | xxxxx | xxxx | 15 | N/A | 8 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-3600 | 3425.2672 | RSV-15-3600 | 90.2 | 1.6297 | 133.2 | 71.1028 | 37.5325 | 33.0878 | 37.302 | 52.7862 | 49.1396 | 53.261 | 1 | 1 | 1 | 1 | 1 | 1 | 1.6297 | 1.6297 | 1.6297 | 54.4159 | 50.7693 | 54.8907 | 53.3533 | 50.8029 | 0.9522 | 133.2 | 71.1028 | 37.5325 | 33.0878 | 37.302 | 52.7862 | 49.1396 | 53.261 | 1 | 1 | 1 | 1 | 1 | 1 | 1.6297 | 1.6297 | 1.6297 | 54.4159 | 50.7693 | 54.8907 | 53.3533 | 1 | 4.7803
#REF! | #REF! | #REF! | IL | N/A | 1800 | No | xxx.xxx.xx | xxxxx | xxxx | 50 | N/A | 5 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | IL-1800 | 1203.8558 | IL-50-1800 | 94.5 | 2.9101 | 129.3 | 72.1709 | 37.5325 | 33.0878 | 37.302 | 52.005 | 48.4124 | 52.4728 | 1 | 0.96825 | 1 | 1 | 0.97776 | 1 | 2.9101 | 2.8453 | 2.9101 | 54.9151 | 51.2577 | 55.3828 | 53.8465 | 50.8029 | 0.94348 | 135.92 | 65.5509 | 37.5325 | 33.0878 | 37.302 | 57.257 | 53.3016 | 57.772 | 1 | 1 | 1 | 1 | 1 | 1 | 2.9101 | 2.9101 | 2.9101 | 60.1671 | 56.2116 | 60.6821 | 59.0144 | 1.096 | 15.2498
#REF! | #REF! | #REF! | ST | N/A | 1800 | No | xxx.xxx.xx | xxxxx | xxxx | 50 | 4 | 5 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-1800 | 1203.8558 | ST-50-1800 | 82.5 | 10.6061 | 138.78 | 62.6909 | 37.5325 | 33.0878 | 37.302 | 59.8691 | 55.7332 | 60.4076 | 1 | 1 | 1 | 1 | 1 | 1 | 10.6061 | 10.6061 | 10.6061 | 70.4752 | 66.3393 | 71.0137 | 69.2691 | 50.8029 | 0.73341 | 138.78 | 62.6909 | 37.5325 | 33.0878 | 37.302 | 59.8691 | 55.7332 | 60.4076 | 1 | 1 | 1 | 1 | 1 | 1 | 10.6061 | 10.6061 | 10.6061 | 70.4752 | 66.3393 | 71.0137 | 69.2691 | 1 | 26.6587

## Section V (Method B.1)
Test Procedure Calculation-Based Approach for Pumps Sold with Motors - Calculation Method (B.1) Section V of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps ---------------------------------------------------------------------------------------------------------------------------------------------------------------------------Test Procedure Calculation-Based Approach for Pumps Sold with Motors - Calculation Method (B.1) Section V of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of PumpsMeasurement of Energy Consumptions of Pumps | [63 empty] | Not part of Calculation Method (A.1) Section III of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps
Initial Database Entry Fields for all Basic Model Listings (Entered by User) | [22 empty] | Universal Lookups & Calculations | [6 empty] | Pump Energy Rating Standard Calculation | [19 empty] | Pump Energy Index Calculation | [13 empty] | HI Energy Rating Calculation for HI 40.5 Energy Rating Program
|  |  |  | nsp | [6 empty] | MotorHP,NP | ηmotor,full,NP | S | Q100% | H100% | P100% | Q75% | H75% | P75% | Q110% | H110% | P110% |  | Ns |  | ηmotor,full | Lfull | LfullNP | C | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | X100% | X75% | X110% | Y100% | Y75% | Y110% | L100% | L75% | L110% | P100%in,M | P75%in,M | P110%in,M | PERCL | PEICL | CBaseline | ƞpump,Baseline | Pu,100% | Pu,75% | Pu,110% | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PEIBaseline | PERBaseline | ER
Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | Rating Load Type | Configuration for which the pump is being rated | DOE Pump Category | If ST - Enter Bowl Diameter (in) | Nominal Speed of rotation | Is motor regulated under 10CFR 431.25? | Participant Company | Basic Model Designation | Basic Model Full Impeller Diameter (in) | If applicable - HI Approved Laboratory Registration Number | Rated Motor Power used for default losses or Nameplate Rated Motor Power | For pumps distributed in commerce with a motor design under 10 CFR Part 431.25, Energy Conservation Program: Energy Conservation Standards for Commercial and Industrial Electric Motors Enter nominal nameplate motor efficiency. Leave blank for ST pumps. All non ST pumps with motors not regulated under 10CFR 431.25, utilize Section III or Section IV | Number of Stages Tested | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 100% of BEP Rate of Flow (hp) | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 75% of BEP Rate of Flow (hp) | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 110% of BEP Rate of Flow (hp) | DOE Equipment Category | Calculate Specific Speed | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Nameplate Full load motor Losses | Lookup Standard C-Value | Calculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Calculate Pump Energy Rating Standard | Calculate pump power input to motor power ratio 100% BEP | Calculate pump power input to motor power ratio 75% BEP | Calculate pump power input to motor power ratio 110% BEP | Calculate Part load loss factor at 100% BEP | Calculate Part load loss factor at 75% BEP | Calculate Part load loss factor at 110% BEP | Calculate part load loss at 100% BEP | Calculate part load loss at 75% BEP | Calculate part load loss at 110% BEP | Calculate driver power input at 100% BEP | Calculate driver power input at 75% BEP | Calculate driver power input at 110% BEP | Calculate Pump Energy Rating Constant Load | Calculate Pump Energy Index Constant Load | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
#REF! | #REF! | #REF! | ESCC | N/A | 3600 | yes | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 60 | 97 | 1 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | ESCC-3600 | 720.0737 | ESCC-60-3600 | 93.6 | 4.1026 | 1.8557 | 130.42 | 60.4576 | 37.5325 | 33.0878 | 37.302 | 62.0807 | 57.792 | 62.6391 | 1 | 0.9632 | 1 | 1 | 0.97421 | 1 | 4.1026 | 3.9968 | 4.1026 | 66.1833 | 61.7888 | 66.7416 | 64.8981 | 0.85691 | 0.82002 | 0.86347 | 0.89924 | 0.87348 | 0.90385 | 1.6687 | 1.6209 | 1.6772 | 53.083 | 50.8222 | 53.4856 | 52.4584 | 0.80832 | 135.94 | 54.9376 | 37.5325 | 33.0878 | 37.302 | 68.3184 | 63.5988 | 68.9329 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1026 | 4.1026 | 4.1026 | 72.421 | 67.7014 | 73.0355 | 71.0455 | 1.0947 | 28.6405
#REF! | #REF! | #REF! | IL | N/A | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 15 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | IL-1800 | 820.7066 | IL-15-1800 | 92.4 | 1.2338 |  | 129.3 | 64.8492 | 37.5325 | 33.0878 | 37.302 | 57.8765 | 53.8783 | 58.3971 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2338 | 1.2338 | 1.2338 | 59.1103 | 55.112 | 59.6308 | 57.9453 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2338 | 1.2338 | 1.2338 | 52.6481 | 50.435 | 53.0421 | 52.0365 | 0.89803 | 135.92 | 58.2292 | 37.5325 | 33.0878 | 37.302 | 64.4564 | 60.0036 | 65.0362 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2338 | 1.2338 | 1.2338 | 65.6902 | 61.2374 | 66.2699 | 64.3927 | 1.1113 | 21.3239
#REF! | #REF! | #REF! | ST | N/A | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 100 | N/A | 4 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | ST-1800 | 1018.338 | ST-100-1800 | 84 | 19.0476 |  | 138.78 | 59.9071 | 37.5325 | 33.0878 | 37.302 | 62.6511 | 58.323 | 63.2147 | 0.62651 | 0.58323 | 0.63215 | 0.74736 | 0.72248 | 0.75071 | 14.2354 | 13.7615 | 14.2993 | 76.8866 | 72.0846 | 77.5139 | 75.4875 | 0.51414 | 0.49201 | 0.51808 | 0.68636 | 0.67584 | 0.68829 | 13.0735 | 12.8732 | 13.1102 | 64.4878 | 62.0745 | 64.9186 | 63.8206 | 0.84545 | 138.78 | 59.9071 | 37.5325 | 33.0878 | 37.302 | 62.6511 | 58.323 | 63.2147 | 0.62651 | 0.58323 | 0.63215 | 0.74736 | 0.72248 | 0.75071 | 14.2354 | 13.7615 | 14.2993 | 76.8866 | 72.0846 | 77.5139 | 75.4875 | 1 | 15.4554
#REF! | #REF! | #REF! | RSV | N/A | 3600 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 25 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | RSV-3600 | 1641.4132 | RSV-25-3600 | 91.7 | 2.2628 |  | 133.2 | 71.7287 | 37.5325 | 33.0878 | 37.302 | 52.3256 | 48.7108 | 52.7963 | 1 | 1 | 1 | 1 | 1 | 1 | 2.2628 | 2.2628 | 2.2628 | 54.5884 | 50.9737 | 55.0591 | 53.535 | 1 | 1 | 1 | 1 | 1 | 1 | 2.2628 | 2.2628 | 2.2628 | 53.6772 | 51.4641 | 54.0712 | 53.0655 | 0.99123 | 133.2 | 71.7287 | 37.5325 | 33.0878 | 37.302 | 52.3256 | 48.7108 | 52.7963 | 1 | 1 | 1 | 1 | 1 | 1 | 2.2628 | 2.2628 | 2.2628 | 54.5884 | 50.9737 | 55.0591 | 53.535 | 1 | 0.87708
#REF! | #REF! | #REF! | IL | N/A | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 100 | N/A | 8 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | IL-1800 | 1712.6336 | IL-100-1800 | 95.4 | 4.8218 |  | 129.3 | 75.9305 | 37.5325 | 33.0878 | 37.302 | 49.43 | 46.0153 | 49.8746 | 0.4943 | 0.46015 | 0.49875 | 0.6769 | 0.6617 | 0.67898 | 3.2639 | 3.1906 | 3.2739 | 52.6939 | 49.2059 | 53.1486 | 51.6776 | 0.51414 | 0.49201 | 0.51808 | 0.68636 | 0.67584 | 0.68829 | 3.3095 | 3.2588 | 3.3188 | 54.7238 | 52.46 | 55.1271 | 54.0983 | 1.0468 | 135.92 | 69.3105 | 37.5325 | 33.0878 | 37.302 | 54.1512 | 50.4103 | 54.6383 | 0.54151 | 0.5041 | 0.54638 | 0.7001 | 0.68152 | 0.70262 | 3.3757 | 3.2862 | 3.3879 | 57.5269 | 53.6965 | 58.0262 | 56.4109 | 1.0916 | 4.4751
#REF! | #REF! | #REF! | ESCC | N/A | 3600 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 75 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | ESCC-3600 | 1641.4132 | ESCC-75-3600 | 93.6 | 5.1282 |  | 130.42 | 74.5087 | 37.5325 | 33.0878 | 37.302 | 50.3733 | 46.8934 | 50.8264 | 0.67164 | 0.62525 | 0.67769 | 0.77487 | 0.74661 | 0.77866 | 3.9737 | 3.8288 | 3.9931 | 54.347 | 50.7222 | 54.8195 | 53.2909 | 0.68552 | 0.65602 | 0.69078 | 0.78361 | 0.76518 | 0.78695 | 4.0185 | 3.924 | 4.0356 | 55.4329 | 53.1252 | 55.844 | 54.7952 | 1.0282 | 135.94 | 68.9887 | 37.5325 | 33.0878 | 37.302 | 54.4038 | 50.6455 | 54.8932 | 0.72538 | 0.67527 | 0.73191 | 0.80936 | 0.77714 | 0.81366 | 4.1506 | 3.9853 | 4.1726 | 58.5544 | 54.6308 | 59.0658 | 57.4113 | 1.0773 | 4.909
#REF! | #REF! | #REF! | IL | N/A | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 100 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | IL-1800 | 820.7066 | IL-100-1800 | 95.4 | 4.8218 |  | 129.3 | 64.8492 | 37.5325 | 33.0878 | 37.302 | 57.8765 | 53.8783 | 58.3971 | 0.57877 | 0.53878 | 0.58397 | 0.72001 | 0.69869 | 0.72289 | 3.4717 | 3.3689 | 3.4856 | 61.3482 | 57.2472 | 61.8827 | 60.1534 | 0.51414 | 0.49201 | 0.51808 | 0.68636 | 0.67584 | 0.68829 | 3.3095 | 3.2588 | 3.3188 | 54.7238 | 52.46 | 55.1271 | 54.0983 | 0.89934 | 135.92 | 58.2292 | 37.5325 | 33.0878 | 37.302 | 64.4564 | 60.0036 | 65.0362 | 0.64456 | 0.60004 | 0.65036 | 0.75818 | 0.73195 | 0.76171 | 3.6558 | 3.5293 | 3.6728 | 68.1122 | 63.5329 | 68.709 | 66.778 | 1.1101 | 21.0791
#REF! | #REF! | #REF! | IL | N/A | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 100 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | IL-1800 | 820.7066 | IL-100-1800 | 95.4 | 4.8218 |  | 129.3 | 64.8492 | 37.5325 | 33.0878 | 37.302 | 57.8765 | 53.8783 | 58.3971 | 0.57877 | 0.53878 | 0.58397 | 0.72001 | 0.69869 | 0.72289 | 3.4717 | 3.3689 | 3.4856 | 61.3482 | 57.2472 | 61.8827 | 60.1534 | 0.51414 | 0.49201 | 0.51808 | 0.68636 | 0.67584 | 0.68829 | 3.3095 | 3.2588 | 3.3188 | 54.7238 | 52.46 | 55.1271 | 54.0983 | 0.89934 | 135.92 | 58.2292 | 37.5325 | 33.0878 | 37.302 | 64.4564 | 60.0036 | 65.0362 | 0.64456 | 0.60004 | 0.65036 | 0.75818 | 0.73195 | 0.76171 | 3.6558 | 3.5293 | 3.6728 | 68.1122 | 63.5329 | 68.709 | 66.778 | 1.1101 | 21.0791
#REF! | #REF! | #REF! | ST | 4 | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 100 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | ST-1800 | 820.7066 | ST-100-1800 | 84 | 19.0476 |  | 138.78 | 55.3692 | 37.5325 | 33.0878 | 37.302 | 67.7858 | 63.103 | 68.3955 | 0.67786 | 0.63103 | 0.68395 | 0.77877 | 0.75005 | 0.78262 | 14.8336 | 14.2866 | 14.907 | 82.6194 | 77.3896 | 83.3025 | 81.0957 | 0.51414 | 0.49201 | 0.51808 | 0.68636 | 0.67584 | 0.68829 | 13.0735 | 12.8732 | 13.1102 | 64.4878 | 62.0745 | 64.9186 | 63.8206 | 0.78698 | 138.78 | 55.3692 | 37.5325 | 33.0878 | 37.302 | 67.7858 | 63.103 | 68.3955 | 0.67786 | 0.63103 | 0.68395 | 0.77877 | 0.75005 | 0.78262 | 14.8336 | 14.2866 | 14.907 | 82.6194 | 77.3896 | 83.3025 | 81.0957 | 1 | 21.3022
#REF! | #REF! | #REF! | IL | N/A | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 200 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | IL-1800 | 820.7066 | IL-200-1800 | 95.8 | 8.7683 |  | 129.3 | 64.8492 | 37.5325 | 33.0878 | 37.302 | 57.8765 | 53.8783 | 58.3971 | 0.28938 | 0.26939 | 0.29199 | 0.60944 | 0.6063 | 0.6099 | 5.3438 | 5.3162 | 5.3478 | 63.2203 | 59.1945 | 63.7449 | 62.047 | 0.25707 | 0.24601 | 0.25904 | 0.60471 | 0.60352 | 0.60495 | 5.3023 | 5.2918 | 5.3044 | 56.7167 | 54.4931 | 57.1127 | 56.1019 | 0.90418 | 135.92 | 58.2292 | 37.5325 | 33.0878 | 37.302 | 64.4564 | 60.0036 | 65.0362 | 0.32228 | 0.30002 | 0.32518 | 0.61608 | 0.61139 | 0.61675 | 5.4019 | 5.3609 | 5.4078 | 69.8584 | 65.3645 | 70.444 | 68.5487 | 1.1048 | 20.0604
#REF! | #REF! | #REF! | IL | N/A | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 30 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | IL-1800 | 820.7066 | IL-30-1800 | 93.6 | 2.0513 |  | 129.3 | 64.8492 | 37.5325 | 33.0878 | 37.302 | 57.8765 | 53.8783 | 58.3971 | 1 | 1 | 1 | 1 | 1 | 1 | 2.0513 | 2.0513 | 2.0513 | 59.9278 | 55.9295 | 60.4484 | 58.7627 | 1 | 1 | 1 | 1 | 1 | 1 | 2.0513 | 2.0513 | 2.0513 | 53.4656 | 51.2525 | 53.8596 | 52.854 | 0.89945 | 135.92 | 58.2292 | 37.5325 | 33.0878 | 37.302 | 64.4564 | 60.0036 | 65.0362 | 1 | 1 | 1 | 1 | 1 | 1 | 2.0513 | 2.0513 | 2.0513 | 66.5077 | 62.0549 | 67.0874 | 65.2102 | 1.1097 | 21.0272
#REF! | #REF! | #REF! | IL | N/A | 1800 | No | xxxxx | xxx.xxx.xx | xxxxx | xxxx | 20 | N/A | 3 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | IL-1800 | 820.7066 | IL-20-1800 | 93 | 1.5054 |  | 129.3 | 64.8492 | 37.5325 | 33.0878 | 37.302 | 57.8765 | 53.8783 | 58.3971 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5054 | 1.5054 | 1.5054 | 59.3819 | 55.3836 | 59.9025 | 58.2168 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5054 | 1.5054 | 1.5054 | 52.9197 | 50.7066 | 53.3137 | 52.3081 | 0.89851 | 135.92 | 58.2292 | 37.5325 | 33.0878 | 37.302 | 64.4564 | 60.0036 | 65.0362 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5054 | 1.5054 | 1.5054 | 65.9618 | 61.509 | 66.5415 | 64.6643 | 1.1107 | 21.2244

## Section VI-a (Method C2)
Testing-based approach for Pumps Sold with Motors & Controls - Calculation Method (C.2) Section IV of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps ---------------------------------------------------------------------Testing-based approach for Pumps Sold with Motors & Controls - Calculation Method (C.2) Section IV of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps ----------------------------------------------------------------------Testing-based approach for Pumps Sold with Motors & Controls - Calculation Method (C.2) Section IV of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps | [71 empty] | Not part of Calculation Method------------------------------------Not part of Calculation Method------------------------------------------Not part of Calculation Method
Initial Database Entry Fields, Set point calculations and Error notification, for all Basic Model Listings (Entered by User)---------------------------------------------------------------------------Initial Database Entry Fields, Set point calculations and Error notification, for all Basic Model Listings (Entered by User)-----------------------------------------------------------Initial Database Entry Fields, Set point calculations and Error notification, for all Basic Model Listings (Entered by User) | [40 empty] | Universal Lookups & Calculations | [5 empty] | Pump Energy Rating Standard Calculation | [19 empty] | Pump Energy Index Calculation |  |  |  |  | HI Energy Rating Calculation for HI 40.5 Energy Rating Program
[5 empty] | nsp |  | MotorHP,NP | ηmotor,full,NP | S | Q100% | H100% | P100%in,C | Q75% | H75% | Q110% | H110% | Q25%,M | Q25%,sp |  | H25%,M | H25%,sp |  | P25%,Min,C | Q50%,M | Q50%,sp |  | H50%,M | H50%,sp |  | P50%,Min,C | Q75%,M | Q75%,sp |  | H75%,M | H75%,sp |  | P75%,Min,C |  |  |  |  | Ns |  | ηmotor,full | Lfull | C | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | P25%,in,C | P50%in,C | P75%in,C | PERVL | PEIVL | CBaseline | ƞpump,Baseline | Pu,100% | Pu,75% | Pu,110% | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PEIBaseline | PERBaseline | ER
Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | Rating Load Type | Configuration for which the pump is being rated | DOE Pump Category | If ST - Enter Bowl Diameter (in) | Nominal Speed of rotation | Is motor regulated under 10CFR 431.25? | Rated Motor Power used for default losses or Nameplate Rated Motor Power | For basic models distributed in commerce with a motor design under 10 CFR Part 431.25, Enter nominal nameplate motor efficiency. Leave blank for ST pumps. All non ST pumps with motors not regulated under 10CFR 431.25, utilize Section III or Section IV | Number of Stages Tested | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Control Power Input at 100% of BEP Rate of Flow (hp) | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Measured variable load flow rate at 25% BEP target (Must be +/- 10% of Q25%,sp) | Target variable load flow rate at 25% BEP target | Q25 % Difference must be less than 10% | Measured variable load head at 25% BEP target | Target variable load head at 25% BEP target | H25 % Difference must be less than 10% | Measured control power input at 25% BEP target | Measured variable load flow rate at 50% BEP target | Target variable load flow rate at 50% BEP target | Q50 % Difference must be less than 10% | Measured variable load head at 50% BEP target | Target variable load head at 50% BEP target | H50 % Difference must be less than 10% | Measured variable load control power input at 50% BEP target | Measured variable load flow rate at 75% BEP target | Target variable load flow rate at 75% BEP target | Q75% Difference must be less than 10% | Measured variable load head at 75% BEP target | Target variable load head at 75% BEP target | H75% Difference must be less than 10% | Measured variable load control power input at 75% BEP target | Basic Model Designation | Basic Model Full Impeller Diameter (in) | If applicable - HI Approved Laboratory Registration Number | DOE Equipment Category | Calculate Specific Speed | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Lookup Standard C-Value | Calculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Calculate Pump Energy Rating Standard | control power input at 25% BEP target flow & head | control power input at 50% BEP target flow & head | control power input at 75% BEP target flow and head | Calculate Pump Energy Rating Variable Load | Calculate Pump Energy Index Variable Load | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
|  |  | ESCC | 4 | 1800 | no | 25 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | ESCC-1800 | 1870.8064 | ESCC-25-1800 | 93.6 | 1.7094 | 128.47 | 77.2556 | 37.5325 | 33.0878 | 37.302 | 48.5822 | 45.226 | 49.0192 | 1 | 1 | 1 | 1 | 1 | 1 | 1.7094 | 1.7094 | 1.7094 | 50.2916 | 46.9354 | 50.7286 | 49.3136 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.62885 | 134.43 | 71.2956 | 37.5325 | 33.0878 | 37.302 | 52.6434 | 49.0067 | 53.1169 | 1 | 1 | 1 | 1 | 1 | 1 | 1.7094 | 1.7094 | 1.7094 | 54.3528 | 50.7161 | 54.8264 | 53.2931 | 1.0807 | 45.185
|  |  | RSV | 4 | 1800 | no | 50 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | RSV-1800 | 1870.8064 | RSV-50-1800 | 94.5 | 2.9101 | 129.63 | 76.0956 | 37.5325 | 33.0878 | 37.302 | 49.3228 | 45.9154 | 49.7664 | 0.98646 | 0.91831 | 0.99533 | 0.99054 | 0.94253 | 0.99674 | 2.8825 | 2.7428 | 2.9006 | 52.2053 | 48.6583 | 52.667 | 51.1717 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.60601 | 129.63 | 76.0956 | 37.5325 | 33.0878 | 37.302 | 49.3228 | 45.9154 | 49.7664 | 0.98646 | 0.91831 | 0.99533 | 0.99054 | 0.94253 | 0.99674 | 2.8825 | 2.7428 | 2.9006 | 52.2053 | 48.6583 | 52.667 | 51.1717 | 1 | 39.3986
|  |  | IL | 4 | 3600 | no | 75 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | IL-3600 | 3741.6129 | IL-75-3600 | 93.6 | 5.1282 | 133.84 | 69.552 | 37.5325 | 33.0878 | 37.302 | 53.9632 | 50.2353 | 54.4485 | 0.71951 | 0.6698 | 0.72598 | 0.80551 | 0.77372 | 0.80975 | 4.1308 | 3.9678 | 4.1526 | 58.094 | 54.203 | 58.6011 | 56.9604 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.54443 | 141.01 | 62.382 | 37.5325 | 33.0878 | 37.302 | 60.1655 | 56.0091 | 60.7067 | 0.80221 | 0.74679 | 0.80942 | 0.86117 | 0.82354 | 0.86614 | 4.4162 | 4.2233 | 4.4418 | 64.5818 | 60.2324 | 65.1484 | 63.3145 | 1.1116 | 56.7127
|  |  | ESCC | 4 | 1800 | no | 100 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | ESCC-1800 | 1870.8064 | ESCC-100-1800 | 95.4 | 4.8218 | 128.47 | 77.2556 | 37.5325 | 33.0878 | 37.302 | 48.5822 | 45.226 | 49.0192 | 0.48582 | 0.45226 | 0.49019 | 0.673 | 0.65839 | 0.675 | 3.2451 | 3.1746 | 3.2547 | 51.8273 | 48.4006 | 52.2739 | 50.8289 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.6101 | 134.43 | 71.2956 | 37.5325 | 33.0878 | 37.302 | 52.6434 | 49.0067 | 53.1169 | 0.52643 | 0.49007 | 0.53117 | 0.69243 | 0.67495 | 0.69481 | 3.3388 | 3.2545 | 3.3502 | 55.9822 | 52.2612 | 56.4672 | 54.898 | 1.0801 | 46.9955
|  |  | ESFM | 4 | 3600 | no | 125 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | ESFM-3600 | 3741.6129 | ESFM-125-3600 | 94.1 | 7.8374 | 130.99 | 72.402 | 37.5325 | 33.0878 | 37.302 | 51.839 | 48.2578 | 52.3052 | 0.41471 | 0.38606 | 0.41844 | 0.64372 | 0.63382 | 0.6451 | 5.0451 | 4.9675 | 5.0559 | 56.8841 | 53.2253 | 57.3611 | 55.8179 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.55557 | 136.59 | 66.802 | 37.5325 | 33.0878 | 37.302 | 56.1846 | 52.3033 | 56.69 | 0.44948 | 0.41843 | 0.45352 | 0.65724 | 0.64509 | 0.65891 | 5.1511 | 5.0559 | 5.1642 | 61.3357 | 57.3591 | 61.8542 | 60.177 | 1.0781 | 52.2524
|  |  | ST | 4 | 1800 | no | 150 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | ST-1800 | 1870.8064 | ST-150-1800 | 85.5 | 25.4386 | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 0.37376 | 0.34794 | 0.37712 | 0.62992 | 0.62247 | 0.63096 | 16.0242 | 15.8347 | 16.0508 | 72.0883 | 68.0258 | 72.6192 | 70.904 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.43736 | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 0.37376 | 0.34794 | 0.37712 | 0.62992 | 0.62247 | 0.63096 | 16.0242 | 15.8347 | 16.0508 | 72.0883 | 68.0258 | 72.6192 | 70.904 | 1 | 56.2637
|  |  | RSV | 4 | 3600 | no | 200 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | RSV-3600 | 3741.6129 | RSV-200-3600 | 95 | 10.5263 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.26736 | 0.24889 | 0.26976 | 0.60602 | 0.60381 | 0.60635 | 6.3792 | 6.3559 | 6.3827 | 59.8503 | 56.1331 | 60.3348 | 58.7668 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.52769 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.26736 | 0.24889 | 0.26976 | 0.60602 | 0.60381 | 0.60635 | 6.3792 | 6.3559 | 6.3827 | 59.8503 | 56.1331 | 60.3348 | 58.7668 | 1 | 47.2308
|  |  | IL | 4 | 3600 | no | 20 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | IL-3600 | 3741.6129 | IL-20-3600 | 91 | 1.978 | 133.84 | 69.552 | 37.5325 | 33.0878 | 37.302 | 53.9632 | 50.2353 | 54.4485 | 1 | 1 | 1 | 1 | 1 | 1 | 1.978 | 1.978 | 1.978 | 55.9412 | 52.2133 | 56.4266 | 54.8549 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.56532 | 141.01 | 62.382 | 37.5325 | 33.0878 | 37.302 | 60.1655 | 56.0091 | 60.7067 | 1 | 1 | 1 | 1 | 1 | 1 | 1.978 | 1.978 | 1.978 | 62.1435 | 57.9872 | 62.6847 | 60.9324 | 1.1108 | 54.5469
|  |  | ESCC | 4 | 3600 | no | 30 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | ESCC-3600 | 3741.6129 | ESCC-30-3600 | 91.7 | 2.7154 | 130.42 | 72.972 | 37.5325 | 33.0878 | 37.302 | 51.4341 | 47.8809 | 51.8967 | 1 | 1 | 1 | 1 | 1 | 1 | 2.7154 | 2.7154 | 2.7154 | 54.1494 | 50.5962 | 54.6121 | 53.1139 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.58385 | 135.94 | 67.452 | 37.5325 | 33.0878 | 37.302 | 55.6432 | 51.7992 | 56.1437 | 1 | 1 | 1 | 1 | 1 | 1 | 2.7154 | 2.7154 | 2.7154 | 58.3586 | 54.5146 | 58.8591 | 57.2384 | 1.0777 | 49.3799
|  |  | ESFM | 4 | 1800 | no | 40 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | ESFM-1800 | 1870.8064 | ESFM-40-1800 | 94.1 | 2.508 | 128.85 | 76.8756 | 37.5325 | 33.0878 | 37.302 | 48.8223 | 45.4496 | 49.2615 | 1 | 1 | 1 | 1 | 1 | 1 | 2.508 | 2.508 | 2.508 | 51.3303 | 47.9575 | 51.7694 | 50.3474 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.61594 | 134.99 | 70.7356 | 37.5325 | 33.0878 | 37.302 | 53.0602 | 49.3947 | 53.5375 | 1 | 1 | 1 | 1 | 1 | 1 | 2.508 | 2.508 | 2.508 | 55.5682 | 51.9027 | 56.0454 | 54.5 | 1.0825 | 46.6543
|  |  | ST | 4 | 3600 | no | 3 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | ST-3600 | 3741.6129 | ST-3-3600 | 70 | 1.2857 | 134.85 | 68.542 | 37.5325 | 33.0878 | 37.302 | 54.7583 | 50.9755 | 55.2509 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2857 | 1.2857 | 1.2857 | 56.044 | 52.2612 | 56.5366 | 54.9418 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.56443 | 138.78 | 64.612 | 37.5325 | 33.0878 | 37.302 | 58.089 | 54.0761 | 58.6115 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2857 | 1.2857 | 1.2857 | 59.3747 | 55.3618 | 59.8972 | 58.2054 | 1.0594 | 49.4972
|  |  | ST | 4 | 3600 | no | 1.5 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | 5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 280 | 275.8793 | 1.494% | 42 |  |  |  | ST-3600 | 3741.6129 | ST-1.5-3600 | 66 | 0.77273 | 134.85 | 68.542 | 37.5325 | 33.0878 | 37.302 | 54.7583 | 50.9755 | 55.2509 | 1 | 1 | 1 | 1 | 1 | 1 | 0.77273 | 0.77273 | 0.77273 | 55.5311 | 51.7482 | 56.0236 | 54.4288 | 10.0869 | 19.9635 | 42.5784 | 31.0108 | 0.56975 | 138.78 | 64.612 | 37.5325 | 33.0878 | 37.302 | 58.089 | 54.0761 | 58.6115 | 1 | 1 | 1 | 1 | 1 | 1 | 0.77273 | 0.77273 | 0.77273 | 58.8617 | 54.8488 | 59.3842 | 57.6925 | 1.06 | 49.0212

## Section VI-b (Method C2)
Testing-based approach for Pumps Sold with Motors & Controls - Calculation Method (C.2) Section IV of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps ---------------------------------------------------------------------Testing-based approach for Pumps Sold with Motors & Controls - Calculation Method (C.2) Section IV of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps ----------------------------------------------------------------------Testing-based approach for Pumps Sold with Motors & Controls - Calculation Method (C.2) Section IV of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps | [71 empty] | Not part of Calculation Method------------------------------------Not part of Calculation Method------------------------------------------Not part of Calculation Method
Initial Database Entry Fields, Set point calculations and Error notification, for all Basic Model Listings (Entered by User)---------------------------------------------------------------------------Initial Database Entry Fields, Set point calculations and Error notification, for all Basic Model Listings (Entered by User)-----------------------------------------------------------Initial Database Entry Fields, Set point calculations and Error notification, for all Basic Model Listings (Entered by User) | [40 empty] | Universal Lookups & Calculations | [5 empty] | Pump Energy Rating Standard Calculation | [19 empty] | Pump Energy Index Calculation |  |  |  |  | HI Energy Rating Calculation for HI 40.5 Energy Rating Program
[5 empty] | nsp |  | MotorHP,NP | ηmotor,full,NP | S | Q100% | H100% | P100%in,C | Q75% | H75% | Q110% | H110% | Q25%,M | Q25%,sp |  | H25%,M | H25%,sp |  | P25%,Min,C | Q50%,M | Q50%,sp |  | H50%,M | H50%,sp |  | P50%,Min,C | Q75%,M | Q75%,sp |  | H75%,M | H75%,sp |  | P75%,Min,C |  |  |  |  | Ns |  | ηmotor,full | Lfull | C | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | P25%,in,C | P50%in,C | P75%in,C | PERVL | PEIVL | CBaseline | ƞpump,Baseline | Pu,100% | Pu,75% | Pu,110% | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PEIBaseline | PERBaseline | ER
Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | Rating Load Type | Configuration for which the pump is being rated | DOE Pump Category | If ST - Enter Bowl Diameter (in) | Nominal Speed of rotation | Is motor regulated under 10CFR 431.25? | Rated Motor Power used for default losses or Nameplate Rated Motor Power | For basic models distributed in commerce with a motor design under 10 CFR Part 431.25, Enter nominal nameplate motor efficiency. Leave blank for ST pumps. All non ST pumps with motors not regulated under 10CFR 431.25, utilize Section III or Section IV | Number of Stages Tested | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Control Power Input at 100% of BEP Rate of Flow (hp) | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Measured variable load flow rate at 25% BEP target (Must be +/- 10% of Q25%,sp) | Target variable load flow rate at 25% BEP target | Q25 % Difference must be less than 10% | Measured variable load head at 25% BEP target | Target variable load head at 25% BEP target | H25 % Difference must be less than 10% below target | Measured control power input at 25% BEP target | Measured variable load flow rate at 50% BEP target | Target variable load flow rate at 50% BEP target | Q50 % Difference must be less than 10% | Measured variable load head at 50% BEP target | Target variable load head at 50% BEP target | H50 % Difference must be less than 10% below target | Measured variable load control power input at 50% BEP target | Measured variable load flow rate at 75% BEP target | Target variable load flow rate at 75% BEP target | Q75% Difference must be less than 10% | Measured variable load head at 75% BEP target | Target variable load head at 75% BEP target | H75 % Difference must be less than 10% below target | Measured variable load control power input at 75% BEP target | Basic Model Designation | Basic Model Full Impeller Diameter (in) | If applicable - HI Approved Laboratory Registration Number | DOE Equipment Category | Calculate Specific Speed | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Lookup Standard C-Value | Calculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Calculate Pump Energy Rating Standard | control power input at 25% BEP target flow & head | control power input at 50% BEP target flow & head | control power input at 75% BEP target flow and head | Calculate Pump Energy Rating Variable Load | git s | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
|  |  | ESCC | 4 | 3600 | no | 150 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | ESCC-3600 | 3741.6129 | ESCC-150-3600 | 94.1 | 9.4049 | 130.42 | 72.972 | 37.5325 | 33.0878 | 37.302 | 51.4341 | 47.8809 | 51.8967 | 0.34289 | 0.31921 | 0.34598 | 0.62113 | 0.61538 | 0.62194 | 5.8417 | 5.7876 | 5.8493 | 57.2757 | 53.6685 | 57.746 | 56.2244 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.56885 | 135.94 | 67.452 | 37.5325 | 33.0878 | 37.302 | 55.6432 | 51.7992 | 56.1437 | 0.37095 | 0.34533 | 0.37429 | 0.62906 | 0.62177 | 0.63008 | 5.9162 | 5.8477 | 5.9258 | 61.5594 | 57.6469 | 62.0695 | 60.4193 | 1.0746 | 50.5758
|  |  | RSV | 4 | 3600 | no | 125 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | RSV-3600 | 3741.6129 | RSV-125-3600 | 94.1 | 7.8374 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.42777 | 0.39822 | 0.43162 | 0.64861 | 0.63788 | 0.6501 | 5.0835 | 4.9993 | 5.0951 | 58.5546 | 54.7765 | 59.0472 | 57.4537 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.55668 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.42777 | 0.39822 | 0.43162 | 0.64861 | 0.63788 | 0.6501 | 5.0835 | 4.9993 | 5.0951 | 58.5546 | 54.7765 | 59.0472 | 57.4537 | 1 | 44.3321
|  |  | IL | 4 | 3600 | no | 100 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | IL-3600 | 3741.6129 | IL-100-3600 | 93.6 | 6.8376 | 133.84 | 69.552 | 37.5325 | 33.0878 | 37.302 | 53.9632 | 50.2353 | 54.4485 | 0.53963 | 0.50235 | 0.54449 | 0.69913 | 0.68069 | 0.70163 | 4.7804 | 4.6543 | 4.7975 | 58.7435 | 54.8895 | 59.246 | 57.6206 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.55507 | 141.01 | 62.382 | 37.5325 | 33.0878 | 37.302 | 60.1655 | 56.0091 | 60.7067 | 0.60166 | 0.56009 | 0.60707 | 0.73288 | 0.70986 | 0.73599 | 5.0111 | 4.8537 | 5.0324 | 65.1766 | 60.8629 | 65.7391 | 63.9198 | 1.1093 | 55.4255
|  |  | ESCC | 4 | 3600 | no | 75 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | ESCC-3600 | 3741.6129 | ESCC-75-3600 | 93.6 | 5.1282 | 130.42 | 72.972 | 37.5325 | 33.0878 | 37.302 | 51.4341 | 47.8809 | 51.8967 | 0.68579 | 0.63841 | 0.69196 | 0.78378 | 0.75447 | 0.7877 | 4.0194 | 3.8691 | 4.0395 | 55.4534 | 51.7499 | 55.9362 | 54.3744 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.5882 | 135.94 | 67.452 | 37.5325 | 33.0878 | 37.302 | 55.6432 | 51.7992 | 56.1437 | 0.74191 | 0.69066 | 0.74858 | 0.82029 | 0.78687 | 0.82474 | 4.2066 | 4.0353 | 4.2294 | 59.8498 | 55.8345 | 60.3731 | 58.6799 | 1.0792 | 49.0979
|  |  | ESFM | 4 | 3600 | no | 60 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | ESFM-3600 | 3741.6129 | ESFM-60-3600 | 93.6 | 4.1026 | 130.99 | 72.402 | 37.5325 | 33.0878 | 37.302 | 51.839 | 48.2578 | 52.3052 | 0.86398 | 0.8043 | 0.87175 | 0.90421 | 0.86261 | 0.90967 | 3.7096 | 3.5389 | 3.732 | 55.5486 | 51.7967 | 56.0372 | 54.4554 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.58733 | 136.59 | 66.802 | 37.5325 | 33.0878 | 37.302 | 56.1846 | 52.3033 | 56.69 | 0.93641 | 0.87172 | 0.94483 | 0.95532 | 0.90965 | 0.96127 | 3.9193 | 3.7319 | 3.9437 | 60.1039 | 56.0352 | 60.6336 | 58.9183 | 1.082 | 49.4626
|  |  | ST | 4 | 3600 | no | 50 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | ST-3600 | 3741.6129 | ST-50-3600 | 80 | 12.5 | 134.85 | 68.542 | 37.5325 | 33.0878 | 37.302 | 54.7583 | 50.9755 | 55.2509 | 1 | 1 | 1 | 1 | 1 | 1 | 12.5 | 12.5 | 12.5 | 67.2583 | 63.4755 | 67.7509 | 66.1549 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.48346 | 138.78 | 64.612 | 37.5325 | 33.0878 | 37.302 | 58.089 | 54.0761 | 58.6115 | 1 | 1 | 1 | 1 | 1 | 1 | 12.5 | 12.5 | 12.5 | 70.589 | 66.5761 | 71.1115 | 69.4186 | 1.0493 | 56.5873
|  |  | RSV | 4 | 3600 | no | 40 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | RSV-3600 | 3741.6129 | RSV-40-3600 | 92.4 | 3.29 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 1 | 1 | 1 | 1 | 1 | 1 | 3.29 | 3.29 | 3.29 | 56.7612 | 53.0673 | 57.2421 | 55.6846 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.57436 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 1 | 1 | 1 | 1 | 1 | 1 | 3.29 | 3.29 | 3.29 | 56.7612 | 53.0673 | 57.2421 | 55.6846 | 1 | 42.5635
|  |  | IL | 4 | 3600 | no | 30 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | IL-3600 | 3741.6129 | IL-30-3600 | 91.7 | 2.7154 | 133.84 | 69.552 | 37.5325 | 33.0878 | 37.302 | 53.9632 | 50.2353 | 54.4485 | 1 | 1 | 1 | 1 | 1 | 1 | 2.7154 | 2.7154 | 2.7154 | 56.6785 | 52.9506 | 57.1639 | 55.5921 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.57532 | 141.01 | 62.382 | 37.5325 | 33.0878 | 37.302 | 60.1655 | 56.0091 | 60.7067 | 1 | 1 | 1 | 1 | 1 | 1 | 2.7154 | 2.7154 | 2.7154 | 62.8809 | 58.7245 | 63.4221 | 61.6697 | 1.1093 | 53.4003
|  |  | ESCC | 4 | 3600 | no | 25 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | ESCC-3600 | 3741.6129 | ESCC-25-3600 | 91.7 | 2.2628 | 130.42 | 72.972 | 37.5325 | 33.0878 | 37.302 | 51.4341 | 47.8809 | 51.8967 | 1 | 1 | 1 | 1 | 1 | 1 | 2.2628 | 2.2628 | 2.2628 | 53.6969 | 50.1437 | 54.1595 | 52.6614 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.60734 | 135.94 | 67.452 | 37.5325 | 33.0878 | 37.302 | 55.6432 | 51.7992 | 56.1437 | 1 | 1 | 1 | 1 | 1 | 1 | 2.2628 | 2.2628 | 2.2628 | 57.906 | 54.0621 | 58.4065 | 56.7858 | 1.0783 | 47.0982
|  |  | ESFM | 4 | 3600 | no | 20 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | ESFM-3600 | 3741.6129 | ESFM-20-3600 | 91 | 1.978 | 130.99 | 72.402 | 37.5325 | 33.0878 | 37.302 | 51.839 | 48.2578 | 52.3052 | 1 | 1 | 1 | 1 | 1 | 1 | 1.978 | 1.978 | 1.978 | 53.817 | 50.2358 | 54.2833 | 52.7734 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.60605 | 136.59 | 66.802 | 37.5325 | 33.0878 | 37.302 | 56.1846 | 52.3033 | 56.69 | 1 | 1 | 1 | 1 | 1 | 1 | 1.978 | 1.978 | 1.978 | 58.1627 | 54.2813 | 58.668 | 57.0316 | 1.0807 | 47.4639
|  |  | ST | 4 | 3600 | no | 15 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 92 | 87.4576 | 5.194% | 100 | 106.1074 | -5.756% | 10 | 170 | 174.9153 | 2.81% | 175 | 169.7719 | 3.079% | 20 | 255 | 262.3729 | 2.81% | 260 | 275.8793 | -5.756% | 42 | #REF! | #REF! | #REF! | ST-3600 | 3741.6129 | ST-15-3600 | 72 | 5.8333 | 134.85 | 68.542 | 37.5325 | 33.0878 | 37.302 | 54.7583 | 50.9755 | 55.2509 | 1 | 1 | 1 | 1 | 1 | 1 | 5.8333 | 5.8333 | 5.8333 | 60.5917 | 56.8088 | 61.0842 | 59.4889 | 10.0869 | 20.5783 | 45.8536 | 31.9833 | 0.53763 | 138.78 | 64.612 | 37.5325 | 33.0878 | 37.302 | 58.089 | 54.0761 | 58.6115 | 1 | 1 | 1 | 1 | 1 | 1 | 5.8333 | 5.8333 | 5.8333 | 63.9223 | 59.9094 | 64.4448 | 62.7526 | 1.0549 | 51.7227

## SectionVII (Method C.1)
Test Procedure Calculation-Based Approach for Pumps Sold with Motors & Controls - Calculation Method (C.1) Section VII of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps ------------------------------------------------------Test Procedure Calculation-Based Approach for Pumps Sold with Motors & Controls - Calculation Method (C.1) Section VII of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps-----------------------------------------------------------------Test Procedure Calculation-Based Approach for Pumps Sold with Motors & Controls - Calculation Method (C.1) Section VII of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps | [72 empty] | Not part of Calculation Method (A.1) Section III of Appendix A to Subpart Y of Part 431 - Uniform Test Methods for the Measurement of Energy Consumptions of Pumps
Initial Database Entry Fields for all Basic Model Listings (Entered by User) | [21 empty] | Universal Lookups & Calculations | [6 empty] | Pump Energy Rating Standard Calculation | [19 empty] | Pump Energy Index Calculation | [23 empty] | HI Energy Rating Calculation for HI 40.5 Energy Rating Program
[5 empty] | nsp |  | MotorHP,NP | ηmotor,full,NP | S | Q100% | H100% | P100% | Q75% | H75% | P75% | Q110% | H110% | P110% |  |  |  |  | Ns |  | ηmotor,full | Lfull | LfullNP | C | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | P25%VL | P50%VL | P75%VL | X100% | X25%VL | X50%VL | X75%VL | a | b | c | Z100% | Z25% | Z50% | Z75% | L100%M,C | L25%M,C | L50%M,C | L75%M,C | P100%in,C | P25%in,C | P50%in,C | P75%in,C | PERVL | PEIVL | CBaseline | ƞpump,Baseline | Pu,100% | Pu,75% | Pu,110% | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PEIBaseline | PERBaseline | ER
Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | Rating Load Type | Configuration for which the pump is being rated | DOE Pump Category | If ST - Enter Bowl Diameter (in) | Nominal Speed of rotation | Is motor regulated under 10CFR 431.25? | Rated Motor Power used for default losses or Nameplate Rated Motor Power | For pumps distributed in commerce with a motor design under 10 CFR Part 431.25, Energy Conservation Program: Energy Conservation Standards for Commercial and Industrial Electric Motors Enter nominal nameplate motor efficiency. N/A for ST pumps. All non ST pumps with motors not regulated under 10CFR 431.25, utilize Section VI for variable load | Number of Stages Tested | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 100% of BEP Rate of Flow (hp) | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 75% of BEP Rate of Flow (hp) | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Pump Power Input at 110% of BEP Rate of Flow (hp) | Basic Model Designation | Basic Model Full Impeller Diameter (in) | If applicable - HI Approved Laboratory Registration Number | DOE Equipment Category | Calculate Specific Speed | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Nameplate Full load motor Losses | Lookup Standard C-Value | Calculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Calculate Pump Energy Rating Standard | Variable load pump power input at 25% BEP Rate of Flow | Variable load pump power input at 50% BEP Rate of Flow | Variable load pump power input at 75% BEP Rate of Flow | Calculate pump power input to motor power ratio 100% BEP | Calculate variable load pump power input to motor power ratio 25% BEP | Calculate variable load pump power input to motor power ratio 50% BEP | Calculate variable load pump power input to motor power ratio 75% BEP | Motor & Control Loss Coefficient "a" | Motor & Control Loss Coefficient "b" | Motor & Control Loss Coefficient "c" | Calculate motor & Control Part load loss factor at 100% BEP | Calculate motor & Control Part load loss factor at 25% BEP | Calculate motor & Control Part load loss factor at 50% BEP | Calculate motor & Control Part load loss factor at 75% BEP | Calculate Motor & Control part load loss at 100% BEP | Calculate Motor & Control part load loss at 25% BEP | Calculate Motor & Control part load loss at 50% BEP | Calculate Motor & Control part load loss at 75% BEP | Calculate control power input at 100% BEP | Calculate Control power input at 25% BEP | Calculate Controlpower input at 50% BEP | Calculate Controlpower input at 75% BEP | Calculate Pump Energy Rating Variable Load | Calculate Pump Energy Index Variable Load | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
#REF! | #REF! | #REF! | ST | 4 | 3600 | yes | 150 | 97 | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-3600 | 3741.6129 | ST-150-3600 | 84 | 28.5714 | 4.6392 | 134.85 | 68.542 | 37.5325 | 33.0878 | 37.302 | 54.7583 | 50.9755 | 55.2509 | 0.36506 | 0.33984 | 0.36834 | 0.62729 | 0.62034 | 0.62827 | 17.9227 | 17.724 | 17.9506 | 72.681 | 68.6994 | 73.2015 | 71.5202 | 3.2134 | 10.2829 | 25.0645 | 0.34276 | 0.021423 | 0.068552 | 0.1671 | -0.8914 | 2.8846 | 0.2625 | 1.1465 | 0.32389 | 0.45606 | 0.71962 | 5.3188 | 1.5026 | 2.1157 | 3.3384 | 56.7332 | 4.716 | 12.3986 | 28.4029 | 25.5627 | 0.35742 | 138.78 | 64.612 | 37.5325 | 33.0878 | 37.302 | 58.089 | 54.0761 | 58.6115 | 0.38726 | 0.36051 | 0.39074 | 0.63421 | 0.62597 | 0.63536 | 18.1202 | 17.8848 | 18.153 | 76.2092 | 71.9609 | 76.7645 | 74.9707 | 1.0482 | 69.0826
#REF! | Variable Load (VL) | Pump sold with motor and continuous controls | ST | 4 | 1800 | no | 150 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-1800 | 1870.8064 | ST-150-1800 | 85.5 | 25.4386 |  | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 0.37376 | 0.34794 | 0.37712 | 0.62992 | 0.62247 | 0.63096 | 16.0242 | 15.8347 | 16.0508 | 72.0883 | 68.0258 | 72.6192 | 70.904 | 3.2134 | 10.2829 | 25.0645 | 0.34276 | 0.021423 | 0.068552 | 0.1671 | -0.8914 | 2.8846 | 0.2625 | 1.1465 | 0.32389 | 0.45606 | 0.71962 | 29.1655 | 8.2392 | 11.6015 | 18.3061 | 80.5798 | 11.4526 | 21.8843 | 43.3706 | 39.3218 | 0.55458 | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 0.37376 | 0.34794 | 0.37712 | 0.62992 | 0.62247 | 0.63096 | 16.0242 | 15.8347 | 16.0508 | 72.0883 | 68.0258 | 72.6192 | 70.904 | 1 | 44.5421
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | RSV | 4 | 3600 | no | 125 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-3600 | 3741.6129 | RSV-125-3600 | 94.1 | 7.8374 |  | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.42777 | 0.39822 | 0.43162 | 0.64861 | 0.63788 | 0.6501 | 5.0835 | 4.9993 | 5.0951 | 58.5546 | 54.7765 | 59.0472 | 57.4537 | 3.2134 | 10.2829 | 25.0645 | 0.41131 | 0.025707 | 0.082263 | 0.20052 | -0.8914 | 2.8846 | 0.2625 | 1.2982 | 0.33607 | 0.49376 | 0.80507 | 10.1743 | 2.6339 | 3.8698 | 6.3096 | 61.5887 | 5.8473 | 14.1527 | 31.3741 | 28.2407 | 0.49154 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.42777 | 0.39822 | 0.43162 | 0.64861 | 0.63788 | 0.6501 | 5.0835 | 4.9993 | 5.0951 | 58.5546 | 54.7765 | 59.0472 | 57.4537 | 1 | 50.8462
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | IL | 4 | 3600 | no | 100 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | IL-3600 | 3741.6129 | IL-100-3600 | 93.6 | 6.8376 |  | 133.84 | 69.552 | 37.5325 | 33.0878 | 37.302 | 53.9632 | 50.2353 | 54.4485 | 0.53963 | 0.50235 | 0.54449 | 0.69913 | 0.68069 | 0.70163 | 4.7804 | 4.6543 | 4.7975 | 58.7435 | 54.8895 | 59.246 | 57.6206 | 3.2134 | 10.2829 | 25.0645 | 0.51414 | 0.032134 | 0.10283 | 0.25064 | -0.8914 | 2.8846 | 0.2625 | 1.51 | 0.35427 | 0.54969 | 0.92951 | 10.3245 | 2.4224 | 3.7586 | 6.3556 | 61.7389 | 5.6358 | 14.0415 | 31.4201 | 28.2091 | 0.48957 | 141.01 | 62.382 | 37.5325 | 33.0878 | 37.302 | 60.1655 | 56.0091 | 60.7067 | 0.60166 | 0.56009 | 0.60707 | 0.73288 | 0.70986 | 0.73599 | 5.0111 | 4.8537 | 5.0324 | 65.1766 | 60.8629 | 65.7391 | 63.9198 | 1.1093 | 61.9757
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ESCC | 4 | 1800 | no | 75 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ESCC-1800 | 1870.8064 | ESCC-75-1800 | 95 | 3.9474 |  | 128.47 | 77.2556 | 37.5325 | 33.0878 | 37.302 | 48.5822 | 45.226 | 49.0192 | 0.64776 | 0.60301 | 0.65359 | 0.76013 | 0.73366 | 0.76369 | 3.0005 | 2.896 | 3.0146 | 51.5827 | 48.122 | 52.0337 | 50.5744 | 3.2134 | 10.2829 | 25.0645 | 0.68552 | 0.042845 | 0.1371 | 0.33419 | -0.8914 | 2.8846 | 0.2625 | 1.8211 | 0.38446 | 0.64124 | 1.127 | 7.1884 | 1.5176 | 2.5312 | 4.4485 | 58.6027 | 4.731 | 12.8141 | 29.513 | 26.4152 | 0.5223 | 134.43 | 71.2956 | 37.5325 | 33.0878 | 37.302 | 52.6434 | 49.0067 | 53.1169 | 0.70191 | 0.65342 | 0.70823 | 0.79409 | 0.76359 | 0.79817 | 3.1346 | 3.0142 | 3.1507 | 55.778 | 52.0209 | 56.2676 | 54.6834 | 1.0812 | 55.8942
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ST | 4 | 3600 | no | 60 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-3600 | 3741.6129 | ST-60-3600 | 81.5 | 13.6196 |  | 134.85 | 68.542 | 37.5325 | 33.0878 | 37.302 | 54.7583 | 50.9755 | 55.2509 | 0.91264 | 0.84959 | 0.92085 | 0.93853 | 0.89411 | 0.94433 | 12.7824 | 12.1774 | 12.8614 | 67.5407 | 63.1529 | 68.1122 | 66.262 | 3.2134 | 10.2829 | 25.0645 | 0.85691 | 0.053557 | 0.17138 | 0.41774 | -0.8914 | 2.8846 | 0.2625 | 2.0798 | 0.41443 | 0.73068 | 1.312 | 28.3259 | 5.6444 | 9.9517 | 17.8684 | 79.7403 | 8.8578 | 20.2345 | 42.9329 | 37.9414 | 0.5726 | 138.78 | 64.612 | 37.5325 | 33.0878 | 37.302 | 58.089 | 54.0761 | 58.6115 | 0.96815 | 0.90127 | 0.97686 | 0.97769 | 0.93049 | 0.98381 | 13.3158 | 12.6729 | 13.3991 | 71.4048 | 66.749 | 72.0106 | 70.0478 | 1.0571 | 48.4537
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | RSV | 4 | 3600 | no | 50 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-3600 | 3741.6129 | RSV-50-3600 | 93 | 3.7634 |  | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 1 | 0.99554 | 1 | 1 | 0.99689 | 1 | 3.7634 | 3.7517 | 3.7634 | 57.2346 | 53.529 | 57.7155 | 56.1541 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.064268 | 0.20566 | 0.50129 | -1.5122 | 3.0777 | 0.1847 | 1.7502 | 0.37625 | 0.75369 | 1.3475 | 6.5868 | 1.416 | 2.8365 | 5.0713 | 58.0011 | 4.6294 | 13.1194 | 30.1358 | 26.4714 | 0.47141 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 1 | 0.99554 | 1 | 1 | 0.99689 | 1 | 3.7634 | 3.7517 | 3.7634 | 57.2346 | 53.529 | 57.7155 | 56.1541 | 1 | 52.8593
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | IL | 4 | 1800 | no | 40 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | IL-1800 | 1870.8064 | IL-40-1800 | 94.1 | 2.508 |  | 129.3 | 76.4256 | 37.5325 | 33.0878 | 37.302 | 49.1098 | 45.7172 | 49.5515 | 1 | 1 | 1 | 1 | 1 | 1 | 2.508 | 2.508 | 2.508 | 51.6178 | 48.2251 | 52.0595 | 50.6291 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.080335 | 0.25707 | 0.62661 | -1.5122 | 3.0777 | 0.1847 | 1.7502 | 0.42219 | 0.87595 | 1.5195 | 4.3894 | 1.0588 | 2.1969 | 3.8108 | 55.8038 | 4.2722 | 12.4797 | 28.8753 | 25.3578 | 0.50085 | 135.92 | 69.8056 | 37.5325 | 33.0878 | 37.302 | 53.7671 | 50.0528 | 54.2507 | 1 | 1 | 1 | 1 | 1 | 1 | 2.508 | 2.508 | 2.508 | 56.2751 | 52.5607 | 56.7587 | 55.1927 | 1.0901 | 58.9284
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ESCC | 4 | 3600 | no | 30 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ESCC-3600 | 3741.6129 | ESCC-30-3600 | 91.7 | 2.7154 |  | 130.42 | 72.972 | 37.5325 | 33.0878 | 37.302 | 51.4341 | 47.8809 | 51.8967 | 1 | 1 | 1 | 1 | 1 | 1 | 2.7154 | 2.7154 | 2.7154 | 54.1494 | 50.5962 | 54.6121 | 53.1139 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.10711 | 0.34276 | 0.83548 | -1.5122 | 3.0777 | 0.1847 | 1.7502 | 0.49701 | 1.062 | 1.7005 | 4.7525 | 1.3496 | 2.8836 | 4.6175 | 56.1668 | 4.563 | 13.1665 | 29.682 | 25.8946 | 0.48753 | 135.94 | 67.452 | 37.5325 | 33.0878 | 37.302 | 55.6432 | 51.7992 | 56.1437 | 1 | 1 | 1 | 1 | 1 | 1 | 2.7154 | 2.7154 | 2.7154 | 58.3586 | 54.5146 | 58.8591 | 57.2384 | 1.0777 | 59.0124
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ST | 4 | 1800 | no | 25 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-1800 | 1870.8064 | ST-25-1800 | 78.5 | 6.8471 |  | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 1 | 1 | 1 | 1 | 1 | 1 | 6.8471 | 6.8471 | 6.8471 | 62.9112 | 59.0382 | 63.4155 | 61.7821 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.12854 | 0.41131 | 1 | -1.5122 | 3.0777 | 0.1847 | 1.7502 | 0.55531 | 1.1948 | 1.7502 | 11.9839 | 3.8023 | 8.1807 | 11.9839 | 63.3982 | 7.0157 | 18.4636 | 37.0484 | 31.4815 | 0.50956 | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 1 | 1 | 1 | 1 | 1 | 1 | 6.8471 | 6.8471 | 6.8471 | 62.9112 | 59.0382 | 63.4155 | 61.7821 | 1 | 49.0444
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | RSV | 4 | 3600 | no | 20 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-3600 | 3741.6129 | RSV-20-3600 | 91 | 1.978 |  | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 1 | 1 | 1 | 1 | 1 | 1 | 1.978 | 1.978 | 1.978 | 55.4492 | 51.7552 | 55.9301 | 54.3727 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.16067 | 0.51414 | 1 | -1.3198 | 2.9551 | 0.1052 | 1.7405 | 0.54593 | 1.2757 | 1.7405 | 3.4427 | 1.0799 | 2.5233 | 3.4427 | 54.8571 | 4.2932 | 12.8062 | 28.5072 | 25.1159 | 0.46192 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 1 | 1 | 1 | 1 | 1 | 1 | 1.978 | 1.978 | 1.978 | 55.4492 | 51.7552 | 55.9301 | 54.3727 | 1 | 53.8078
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | IL | 4 | 1800 | no | 15 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | IL-1800 | 1870.8064 | IL-15-1800 | 92.4 | 1.2338 |  | 129.3 | 76.4256 | 37.5325 | 33.0878 | 37.302 | 49.1098 | 45.7172 | 49.5515 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2338 | 1.2338 | 1.2338 | 50.3436 | 46.9509 | 50.7853 | 49.355 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.21423 | 0.68552 | 1 | -1.3198 | 2.9551 | 0.1052 | 1.7405 | 0.67769 | 1.5108 | 1.7405 | 2.1474 | 0.83611 | 1.8639 | 2.1474 | 53.5617 | 4.0495 | 12.1468 | 27.2119 | 24.2425 | 0.49119 | 135.92 | 69.8056 | 37.5325 | 33.0878 | 37.302 | 53.7671 | 50.0528 | 54.2507 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2338 | 1.2338 | 1.2338 | 55.0009 | 51.2865 | 55.4845 | 53.9186 | 1.0925 | 60.1279
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ESCC | 4 | 3600 | no | 10 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ESCC-3600 | 3741.6129 | ESCC-10-3600 | 89.5 | 1.1732 |  | 130.42 | 72.972 | 37.5325 | 33.0878 | 37.302 | 51.4341 | 47.8809 | 51.8967 | 1 | 1 | 1 | 1 | 1 | 1 | 1.1732 | 1.1732 | 1.1732 | 52.6072 | 49.054 | 53.0699 | 51.5719 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.32134 | 1 | 1 | -1.3198 | 2.9551 | 0.1052 | 1.7405 | 0.91851 | 1.7405 | 1.7405 | 2.0419 | 1.0776 | 2.0419 | 2.0419 | 53.4563 | 4.291 | 12.3248 | 27.1064 | 24.2946 | 0.47108 | 135.94 | 67.452 | 37.5325 | 33.0878 | 37.302 | 55.6432 | 51.7992 | 56.1437 | 1 | 1 | 1 | 1 | 1 | 1 | 1.1732 | 1.1732 | 1.1732 | 56.8164 | 52.9724 | 57.3169 | 55.6963 | 1.08 | 60.8892
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ST | 4 | 1800 | no | 7.5 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-1800 | 1870.8064 | ST-7.5-1800 | 74 | 2.6351 |  | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 1 | 1 | 1 | 1 | 1 | 1 | 2.6351 | 2.6351 | 2.6351 | 58.6993 | 54.8262 | 59.2035 | 57.5706 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.42845 | 1 | 1 | -1.3198 | 2.9551 | 0.1052 | 1.7405 | 1.129 | 1.7405 | 1.7405 | 4.5865 | 2.9752 | 4.5865 | 4.5865 | 56.0008 | 6.1886 | 14.8693 | 29.6509 | 26.6774 | 0.46339 | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 1 | 1 | 1 | 1 | 1 | 1 | 2.6351 | 2.6351 | 2.6351 | 58.6993 | 54.8262 | 59.2035 | 57.5706 | 1 | 53.6614
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | RSV | 4 | 3600 | no | 5 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | RSV-3600 | 3741.6129 | RSV-5-3600 | 86.5 | 0.78035 |  | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 1 | 1 | 1 | 1 | 1 | 1 | 0.78035 | 0.78035 | 0.78035 | 54.2515 | 50.5576 | 54.7324 | 53.1752 | 3.2134 | 10.2829 | 25.0645 | 1 | 0.64268 | 1 | 1 | -0.4658 | 1.4965 | 0.5303 | 1.561 | 1.2997 | 1.561 | 1.561 | 1.2181 | 1.0142 | 1.2181 | 1.2181 | 52.6325 | 4.2276 | 11.501 | 26.2826 | 23.6609 | 0.44496 | 133.2 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 1 | 1 | 1 | 1 | 1 | 1 | 0.78035 | 0.78035 | 0.78035 | 54.2515 | 50.5576 | 54.7324 | 53.1752 | 1 | 55.5038
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | IL | 4 | 1800 | no | 3 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | IL-1800 | 1870.8064 | IL-3-1800 | 89.5 | 0.35196 |  | 129.3 | 76.4256 | 37.5325 | 33.0878 | 37.302 | 49.1098 | 45.7172 | 49.5515 | 1 | 1 | 1 | 1 | 1 | 1 | 0.35196 | 0.35196 | 0.35196 | 49.4618 | 46.0691 | 49.9035 | 48.4733 | 3.2134 | 10.2829 | 25.0645 | 1 | 1 | 1 | 1 | -0.4658 | 1.4965 | 0.5303 | 1.561 | 1.561 | 1.561 | 1.561 | 0.5494 | 0.5494 | 0.5494 | 0.5494 | 51.9638 | 3.7628 | 10.8323 | 25.6139 | 23.0432 | 0.47538 | 135.92 | 69.8056 | 37.5325 | 33.0878 | 37.302 | 53.7671 | 50.0528 | 54.2507 | 1 | 1 | 1 | 1 | 1 | 1 | 0.35196 | 0.35196 | 0.35196 | 54.1191 | 50.4047 | 54.6027 | 53.0369 | 1.0941 | 61.8767
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ESCC | 4 | 3600 | no | 2 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ESCC-3600 | 3741.6129 | ESCC-2-3600 | 85.5 | 0.33918 |  | 130.42 | 72.972 | 37.5325 | 33.0878 | 37.302 | 51.4341 | 47.8809 | 51.8967 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33918 | 0.33918 | 0.33918 | 51.7732 | 48.22 | 52.2359 | 50.738 | 3.2134 | 10.2829 | 25.0645 | 1 | 1 | 1 | 1 | -0.4658 | 1.4965 | 0.5303 | 1.561 | 1.561 | 1.561 | 1.561 | 0.52946 | 0.52946 | 0.52946 | 0.52946 | 51.9438 | 3.7429 | 10.8123 | 25.594 | 23.0232 | 0.45377 | 135.94 | 67.452 | 37.5325 | 33.0878 | 37.302 | 55.6432 | 51.7992 | 56.1437 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33918 | 0.33918 | 0.33918 | 55.9824 | 52.1384 | 56.4829 | 54.8624 | 1.0813 | 62.7521
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ST | 4 | 1800 | no | 1.5 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-1800 | 1870.8064 | ST-1.5-1800 | 70 | 0.64286 |  | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 1 | 1 | 1 | 1 | 1 | 1 | 0.64286 | 0.64286 | 0.64286 | 56.707 | 52.8339 | 57.2112 | 55.5785 | 3.2134 | 10.2829 | 25.0645 | 1 | 1 | 1 | 1 | -0.4658 | 1.4965 | 0.5303 | 1.561 | 1.561 | 1.561 | 1.561 | 1.0035 | 1.0035 | 1.0035 | 1.0035 | 52.4179 | 4.2169 | 11.2864 | 26.068 | 23.4973 | 0.42278 | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 1 | 1 | 1 | 1 | 1 | 1 | 0.64286 | 0.64286 | 0.64286 | 56.707 | 52.8339 | 57.2112 | 55.5785 | 1 | 57.7224
Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ST | 4 | 1800 | no | 1 | N/A | 9 | 349.8305 | 424.4298 | 51.4144 | 262.3729 | 498.8911 | 49.2013 | 384.8136 | 383.476 | 51.8084 | xxx.xxx.xx | xxxxx | xxxx | ST-1800 | 1870.8064 | ST-1-1800 | 68 | 0.47059 |  | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 1 | 1 | 1 | 1 | 1 | 1 | 0.47059 | 0.47059 | 0.47059 | 56.5347 | 52.6617 | 57.039 | 55.4062 | 3.2134 | 10.2829 | 25.0645 | 1 | 1 | 1 | 1 | -0.4658 | 1.4965 | 0.5303 | 1.561 | 1.561 | 1.561 | 1.561 | 0.73459 | 0.73459 | 0.73459 | 0.73459 | 52.1489 | 3.948 | 11.0175 | 25.7991 | 23.2284 | 0.41924 | 138.78 | 66.9456 | 37.5325 | 33.0878 | 37.302 | 56.0641 | 52.1911 | 56.5684 | 1 | 1 | 1 | 1 | 1 | 1 | 0.47059 | 0.47059 | 0.47059 | 56.5347 | 52.6617 | 57.039 | 55.4062 | 1 | 58.0763

## Lookup
Bare Pump
Pump sold with motor
Pump sold with motor and continuous controls
Pump sold with motor and non-continuous controls
| ESCC-1800 |  | ESCC | 3600 |  | Constant Load (CL) | ESCC-1800 | 1.09 |  |  | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve
| ESCC-3600 |  | ESFM | 1800 |  | Variable Load (VL) | ESCC-3600 | 1.09 |  |  | Section V - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor part Load Loss Curve
| ESFM-1800 |  | IL |  |  |  | ESFM-1800 | 1.1 |  |  | Section IV - Pump + Motor Tested Wire-to-Water Performance
| ESFM-3600 |  | RSV |  |  |  | ESFM-3600 | 1.09 |  |  | Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve
| IL-1800 |  | ST |  |  |  | IL-1800 | 1.11 |  |  | Section VI - Pump + Motor + Control Tested Wire-to-Water Performance + Assumed Control Curve
| IL-3600 | [5 empty] | IL-3600 | 1.13
| RSV-1800 | [5 empty] | RSV-1800 | 1
| RSV-3600 | [5 empty] | RSV-3600 | 1
| ST-1800 | [5 empty] | ST-1800 | 1
| ST-3600 | [5 empty] | ST-3600 | 1.07
[6 empty] | N/A |  |  |  |  | DOE Equipment Category | C-value |  | Default Nominal Full Load Nominal Efficiency [ESCC, ESFM, IL, RSV & ST] |  |  | or horsepower/
[6 empty] | 1 | [5 empty] | Baseline | Standard | Motor Horsepower [MotorHP] | Efficiency (%) [ηmotor,full] |  | standard kilowatt equivalent
|  |  | 250 |  | 1 | 2 |  |  |  |  | ESCC-1800 | 134.43 | 128.47 |  | 1800 rpm | 3600 rpm |  | 2Pole | 4 Pole
|  |  | 200 |  | 1.5 | 3 |  |  |  |  | ESCC-3600 | 135.94 | 130.42 | ESCC-250-1800 | 95.8 | 95 | 1 | 77 | 85.5
|  |  | 150 |  | 2 | 4 |  |  |  |  | ESFM-1800 | 134.99 | 128.85 | ESCC-200-1800 | 95.8 | 95 | 1.5 | 84 | 86.5
|  |  | 125 |  | 3 | 6 |  |  |  |  | ESFM-3600 | 136.59 | 130.99 | ESCC-150-1800 | 95.8 | 94.1 | 2 | 85.5 | 86.5
|  |  | 100 |  | 5 | [5 empty] | IL-1800 | 135.92 | 129.3 | ESCC-125-1800 | 95.4 | 94.1 | 3 | 85.5 | 89.5
|  |  | 75 |  | 7.5 | [5 empty] | IL-3600 | 141.01 | 133.84 | ESCC-100-1800 | 95.4 | 93.6 | 5 | 86.5 | 89.5
|  |  | 60 |  | 10 | [5 empty] | RSV-1800 | 129.63 | 129.63 | ESCC-75-1800 | 95 | 93.6 | 7.5 | 88.5 | 91
|  |  | 50 |  | 15 | [5 empty] | RSV-3600 | 133.2 | 133.2 | ESCC-60-1800 | 95 | 93.6 | 10 | 89.5 | 91.7
|  |  | 40 |  | 20 | [5 empty] | ST-1800 | 138.78 | 138.78 | ESCC-50-1800 | 94.5 | 93 | 15 | 90.2 | 92.4
|  |  | 30 |  | 25 | Yes |  |  |  |  | ST-3600 | 138.78 | 134.85 | ESCC-40-1800 | 94.1 | 92.4 | 20 | 91 | 93
|  |  | 25 |  | 30 | No | [7 empty] | ESCC-30-1800 | 93.6 | 91.7 | 25 | 91.7 | 93.6
|  |  | 20 |  | 40 | N/A | [7 empty] | ESCC-25-1800 | 93.6 | 91.7 | 30 | 91.7 | 93.6
|  |  | 15 |  | 50 | [8 empty] | ESCC-20-1800 | 93 | 91 | 40 | 92.4 | 94.1
|  |  | 10 |  | 60 | [8 empty] | ESCC-15-1800 | 92.4 | 90.2 | 50 | 93 | 94.5
|  |  | 7.5 |  | 75 | [8 empty] | ESCC-10-1800 | 91.7 | 89.5 | 60 | 93.6 | 95
|  |  | 5 |  | 100 | [8 empty] | ESCC-7.5-1800 | 91 | 88.5 | 75 | 93.6 | 95
|  |  | 3 |  | 125 | [8 empty] | ESCC-5-1800 | 89.5 | 86.5 | 100 | 93.6 | 95.4
|  |  | 2 |  | 150 | [8 empty] | ESCC-3-1800 | 89.5 | 85.5 | 125 | 94.1 | 95.4
|  |  | 1.5 |  | 200 | [8 empty] | ESCC-2-1800 | 86.5 | 85.5 | 150 | 94.1 | 95.8
|  |  | 1 |  | 250 | [8 empty] | ESCC-1.5-1800 | 86.5 | 84 | 200 | 95 | 95.8
[14 empty] | ESCC-1-1800 | 85.5 | 77 | 250 | 95 | 95.8
[14 empty] | ESCC-250-3600 | 95
[14 empty] | ESCC-200-3600 | 95
[14 empty] | ESCC-150-3600 | 94.1
[14 empty] | ESCC-125-3600 | 94.1
[14 empty] | ESCC-100-3600 | 93.6
[14 empty] | ESCC-75-3600 | 93.6
[14 empty] | ESCC-60-3600 | 93.6
1.15 | [13 empty] | ESCC-50-3600 | 93
ST |  |  | Motor Rating | Coefficients for Motor & Control Part Load loss Factor Zi | [9 empty] | ESCC-40-3600 | 92.4
|  |  |  | a | b | c | [7 empty] | ESCC-30-3600 | 91.7
|  | 200 | MotorHP,NP > 50 | -0.8914 | 2.8846 | 0.2625 | MotorHP,NP ≤ 5 | -0.4658 | 1.4965 | 0.5303 |  |  |  | ESCC-25-3600 | 91.7
|  | 50 | MotorHP,NP > 20 and ≤ 50 | -1.5122 | 3.0777 | 0.1847 | MotorHP,NP > 5 and ≤ 20 | -1.3198 | 2.9551 | 0.1052 |  |  |  | ESCC-20-3600 | 91
yes |  | 20 | MotorHP,NP > 5 and ≤ 20 | -1.3198 | 2.9551 | 0.1052 | MotorHP,NP > 20 and ≤ 50 | -1.5122 | 3.0777 | 0.1847 |  |  |  | ESCC-15-3600 | 90.2
no |  | 5 | MotorHP,NP ≤ 5 | -0.4658 | 1.4965 | 0.5303 | MotorHP,NP > 50 | -0.8914 | 2.8846 | 0.2625 |  |  |  | ESCC-10-3600 | 89.5
[14 empty] | ESCC-7.5-3600 | 88.5
[14 empty] | ESCC-5-3600 | 86.5
[14 empty] | ESCC-3-3600 | 85.5
[14 empty] | ESCC-2-3600 | 85.5
[14 empty] | ESCC-1.5-3600 | 84
[14 empty] | ESCC-1-3600 | 77
[14 empty] | ESFM-250-1800 | 95.8
[14 empty] | ESFM-200-1800 | 95.8
[14 empty] | ESFM-150-1800 | 95.8
[14 empty] | ESFM-125-1800 | 95.4
[14 empty] | ESFM-100-1800 | 95.4
[14 empty] | ESFM-75-1800 | 95
[14 empty] | ESFM-60-1800 | 95
[14 empty] | ESFM-50-1800 | 94.5
[14 empty] | ESFM-40-1800 | 94.1
[14 empty] | ESFM-30-1800 | 93.6
[14 empty] | ESFM-25-1800 | 93.6
[14 empty] | ESFM-20-1800 | 93
[14 empty] | ESFM-15-1800 | 92.4
[14 empty] | ESFM-10-1800 | 91.7
[14 empty] | ESFM-7.5-1800 | 91
[14 empty] | ESFM-5-1800 | 89.5
[14 empty] | ESFM-3-1800 | 89.5
[14 empty] | ESFM-2-1800 | 86.5
[14 empty] | ESFM-1.5-1800 | 86.5
[14 empty] | ESFM-1-1800 | 85.5
[14 empty] | ESFM-250-3600 | 95
[14 empty] | ESFM-200-3600 | 95
[14 empty] | ESFM-150-3600 | 94.1
[14 empty] | ESFM-125-3600 | 94.1
[14 empty] | ESFM-100-3600 | 93.6
[14 empty] | ESFM-75-3600 | 93.6
[14 empty] | ESFM-60-3600 | 93.6
[14 empty] | ESFM-50-3600 | 93
[14 empty] | ESFM-40-3600 | 92.4
[14 empty] | ESFM-30-3600 | 91.7
[14 empty] | ESFM-25-3600 | 91.7
[14 empty] | ESFM-20-3600 | 91
[14 empty] | ESFM-15-3600 | 90.2
[14 empty] | ESFM-10-3600 | 89.5
[14 empty] | ESFM-7.5-3600 | 88.5
[14 empty] | ESFM-5-3600 | 86.5
[14 empty] | ESFM-3-3600 | 85.5
[14 empty] | ESFM-2-3600 | 85.5
[14 empty] | ESFM-1.5-3600 | 84
[14 empty] | ESFM-1-3600 | 77
[14 empty] | IL-250-1800 | 95.8
[14 empty] | IL-200-1800 | 95.8
[14 empty] | IL-150-1800 | 95.8
[14 empty] | IL-125-1800 | 95.4
[14 empty] | IL-100-1800 | 95.4
[14 empty] | IL-75-1800 | 95
[14 empty] | IL-60-1800 | 95
[14 empty] | IL-50-1800 | 94.5
[14 empty] | IL-40-1800 | 94.1
[14 empty] | IL-30-1800 | 93.6
[14 empty] | IL-25-1800 | 93.6
[14 empty] | IL-20-1800 | 93
[14 empty] | IL-15-1800 | 92.4
[14 empty] | IL-10-1800 | 91.7
[14 empty] | IL-7.5-1800 | 91
[14 empty] | IL-5-1800 | 89.5
[14 empty] | IL-3-1800 | 89.5
[14 empty] | IL-2-1800 | 86.5
[14 empty] | IL-1.5-1800 | 86.5
[14 empty] | IL-1-1800 | 85.5
[14 empty] | IL-250-3600 | 95
[14 empty] | IL-200-3600 | 95
[14 empty] | IL-150-3600 | 94.1
[14 empty] | IL-125-3600 | 94.1
[14 empty] | IL-100-3600 | 93.6
[14 empty] | IL-75-3600 | 93.6
[14 empty] | IL-60-3600 | 93.6
[14 empty] | IL-50-3600 | 93
[14 empty] | IL-40-3600 | 92.4
[14 empty] | IL-30-3600 | 91.7
[14 empty] | IL-25-3600 | 91.7
[14 empty] | IL-20-3600 | 91
[14 empty] | IL-15-3600 | 90.2
[14 empty] | IL-10-3600 | 89.5
[14 empty] | IL-7.5-3600 | 88.5
[14 empty] | IL-5-3600 | 86.5
[14 empty] | IL-3-3600 | 85.5
[14 empty] | IL-2-3600 | 85.5
[14 empty] | IL-1.5-3600 | 84
[14 empty] | IL-1-3600 | 77
[14 empty] | RSV-250-1800 | 95.8
[14 empty] | RSV-200-1800 | 95.8
[14 empty] | RSV-150-1800 | 95.8
[14 empty] | RSV-125-1800 | 95.4
[14 empty] | RSV-100-1800 | 95.4
[14 empty] | RSV-75-1800 | 95
[14 empty] | RSV-60-1800 | 95
[14 empty] | RSV-50-1800 | 94.5
[14 empty] | RSV-40-1800 | 94.1
[14 empty] | RSV-30-1800 | 93.6
[14 empty] | RSV-25-1800 | 93.6
[14 empty] | RSV-20-1800 | 93
[14 empty] | RSV-15-1800 | 92.4
[14 empty] | RSV-10-1800 | 91.7
[14 empty] | RSV-7.5-1800 | 91
[14 empty] | RSV-5-1800 | 89.5
[14 empty] | RSV-3-1800 | 89.5
[14 empty] | RSV-2-1800 | 86.5
[14 empty] | RSV-1.5-1800 | 86.5
[14 empty] | RSV-1-1800 | 85.5
[14 empty] | RSV-250-3600 | 95
[14 empty] | RSV-200-3600 | 95
[14 empty] | RSV-150-3600 | 94.1
[14 empty] | RSV-125-3600 | 94.1
[14 empty] | RSV-100-3600 | 93.6
[14 empty] | RSV-75-3600 | 93.6
[14 empty] | RSV-60-3600 | 93.6
[14 empty] | RSV-50-3600 | 93
[14 empty] | RSV-40-3600 | 92.4
[14 empty] | RSV-30-3600 | 91.7
[14 empty] | RSV-25-3600 | 91.7
[14 empty] | RSV-20-3600 | 91
[14 empty] | RSV-15-3600 | 90.2
[14 empty] | RSV-10-3600 | 89.5
[14 empty] | RSV-7.5-3600 | 88.5
[14 empty] | RSV-5-3600 | 86.5
[14 empty] | RSV-3-3600 | 85.5
[14 empty] | RSV-2-3600 | 85.5
[14 empty] | RSV-1.5-3600 | 84
[14 empty] | RSV-1-3600 | 77
[14 empty] | ST-250-1800 | 86.5
[14 empty] | ST-200-1800 | 86.5
[14 empty] | ST-150-1800 | 85.5
[14 empty] | ST-125-1800 | 84
[14 empty] | ST-100-1800 | 84
[14 empty] | ST-75-1800 | 85.5
[14 empty] | ST-60-1800 | 84
[14 empty] | ST-50-1800 | 82.5
[14 empty] | ST-40-1800 | 81.5
[14 empty] | ST-30-1800 | 80
[14 empty] | ST-25-1800 | 78.5
[14 empty] | ST-20-1800 | 77
[14 empty] | ST-15-1800 | 75.5
[14 empty] | ST-10-1800 | 74
[14 empty] | ST-7.5-1800 | 74
[14 empty] | ST-5-1800 | 75.5
[14 empty] | ST-3-1800 | 75.5
[14 empty] | ST-2-1800 | 70
[14 empty] | ST-1.5-1800 | 70
[14 empty] | ST-1-1800 | 68
[14 empty] | ST-250-3600 | 86.5
[14 empty] | ST-200-3600 | 85.5
[14 empty] | ST-150-3600 | 84
[14 empty] | ST-125-3600 | 84
[14 empty] | ST-100-3600 | 81.5
[14 empty] | ST-75-3600 | 81.5
[14 empty] | ST-60-3600 | 81.5
[14 empty] | ST-50-3600 | 80
[14 empty] | ST-40-3600 | 78.5
[14 empty] | ST-30-3600 | 77
[14 empty] | ST-25-3600 | 74
[14 empty] | ST-20-3600 | 72
[14 empty] | ST-15-3600 | 72
[14 empty] | ST-10-3600 | 70
[14 empty] | ST-7.5-3600 | 68
[14 empty] | ST-5-3600 | 74
[14 empty] | ST-3-3600 | 70
[14 empty] | ST-2-3600 | 68
[14 empty] | ST-1.5-3600 | 66
[14 empty] | ST-1-3600 | 55

## HI 40.5 database fields
All database entry fields should be able to imported from any one of the calculation method tabs (Section III, Section IV, Section V, Section VI or Section VII. Note Secondary Fields differ by Section
Initial Database Entry Fields for all Basic Model Listings-------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings
[6 empty] | nsp |  | MotorHP or MotorHP,NP |  | Q100% | H100% | Q75% | H75% | Q110% | H110% |  | S |  | PEICL or PEIVL
Participant Company | Basic Model Designation | Rating Load Type | Configuration for which the pump is being rated | Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | DOE Pump Category | Nominal Speed of rotation | DOE Equipment Category | Rated Motor Power used for default losses or Nameplate Rated Motor Power (MotorHP) | MotorHP and Speed | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Basic Model Full Impeller Diameter (in) | Number of Stages Tested | HI Approved Laboratory Registration Number | Enter PEI for Basic Model to be listed
xxxxx | xxx.xxx.xx | Constant Load (CL) | Bare Pump | Section V - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor part Load Loass Curve | ST | 3600 | ST-3600 | 60 | 60-3600 | 349.83 | 424.43 | 262.37 | 498.89 | 384.81 | 383.48 | xxxxx | 9 | xxxx | 0.95
User enter - freeform entry | User Enter - Free form entered | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter -Dropdown menu | User Enter - Dropdown menu | Calculation Combination of cells C & D | User dropdown | Calculation Combination of cells L & D | User enter - Freeform entry
| This is a unique designation for the product to be rated. Refer to 10 CFRxxxx |  |  | If CL is selected - Only sections III, IV and V are available If VL is selected - only section VI and VII are available | [13 empty] | Needs to communicate with HI PTLAP database to ensure it is a valid certificate number
Secondary Database Entry Fields based on initial fields entered
If Cell E4 is DOE Equipment Category - ST-3600 or ST-1800
If PEI Calculation Methods Section III |  |  |  | or | If PEI Calculation Methods Section IV or V |  |  |  | or | If PEI Calculation Methods Section VI or VII
P75%in,M | P100%in,M | P110%in,M |  |  | P75%in,M | P100%in,M | P110%in,M |  |  | P25%in,C | P50%in,C | P75%in,C | P110%in,C
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Bowl diameter (in) |  | Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Bowl diameter (in) |  | Control Input Power at 25% of BEP Rate of Flow (hp) | Control Input Power at 50% of BEP Rate of Flow (hp) | Control Input Power at 75% of BEP Rate of Flow (hp) | Control Input Power at 100% of BEP Rate of Flow (hp) | Bowl diameter (in)
35 | 40 | 45 | 4 |  | 35 | 40 | 45 | 4 |  | 2.5 | 10 | 18 | 40 | 4
User Enter - freeform entry |  |  | User Enter - Dropdown menu |  | User Enter - freeform entry |  |  | User Enter - Dropdown menu |  | User Enter - freeform entry |  |  |  | User Enter - Dropdown menu
OR
If Cell E4 DOE Equipment Category - ESCC-1800, ESCC-3600, ESFM-1800, ESFM-3600, IL-1800, IL-3600, RSV-1800 or RSV-3600
If PEI Calculation Methods Section III |  |  | or | If PEI Calculation Methods Section IV or V |  |  |  |  | or | If PEI Calculation Methods Section VI or VII
P75%in,M | P100%in,M | P110%in,M |  | P75%in,M | P100%in,M | P110%in,M |  |  |  | P25%in,C | P50%in,C | P75%in,C | P110%in,C
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) |  | Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Is motor regulated under 10 CFR 431.25 | If Yes - Nameplate nominal motor efficiency (%) |  | Control Input Power at 25% of BEP Rate of Flow (hp) | Control Input Power at 50% of BEP Rate of Flow (hp) | Control Input Power at 75% of BEP Rate of Flow (hp) | Control Input Power at 100% of BEP Rate of Flow (hp) | Is motor regulated under 10 CFR 431.25 | If Yes - Nameplate nominal motor efficiency (%)
35 | 40 | 45 |  | 35 | 40 | 45 | Yes | 95 |  | 2.5 | 10 | 18 | 40 | Yes | 95
User Enter - freeform entry |  |  |  | User Enter - freeform entry |  |  | User Enter - Dropdown menu | User Enter - freeform entry |  | User Enter - freeform entry |  |  |  | User Enter - Dropdown menu | User Enter - freeform entry
Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating----------------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating-----------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating
Ns | C | CBaseline |  | ηmotor,full | Lfull | ƞpump,STD | ƞpump,Baseline | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | P100%Baseline | P75%Baseline | P110%Baseline | X100%STD | X75%STD | X110%STD | X100%Baseline | X75%Baseline | X110%Baseline | Y100%STD | Y75%STD | Y110%STD | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%STD | L75%STD | L110%STD | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,STD | P75%in,STD | P110%in,STD | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERSTD | PERBaseline | PEIBaseline | ER
Calculate Specifc Speed | Lookup Standard C-Value | Lookup baseline C-Value | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Caculate Std pump Efficiency | Calculate baseline pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Standard | Caclculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
3741.6086 | 134.85 | 138.78 | ST-60-3600 | 81.5 | 13.6196 | 68.542 | 64.612 | 37.5324 | 33.0874 | 37.3021 | 54.7583 | 50.9748 | 55.2509 | 58.0889 | 54.0753 | 58.6115 | 0.91264 | 0.84958 | 0.92085 | 0.96815 | 0.90126 | 0.97686 | 0.93852 | 0.8941 | 0.94433 | 0.97769 | 0.93048 | 0.98381 | 12.7824 | 12.1773 | 12.8614 | 13.3158 | 12.6728 | 13.3991 | 67.5406 | 63.1521 | 68.1123 | 71.4047 | 66.7482 | 72.0106 | 66.2617 | 70.0475 | 1.0571 | 10.7134
calculation | Lookup | Lookup | Calculation Combination of cells C, L & D for later lookup | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation
#REF!