## Database Input Tab all Sections
Participant Company
xxxxx
Initial Database Entry Fields for all Basic Model Listings (Entered by User) -----Initial Database Entry Fields for all Basic Model Listings (Entered by User)-------Initial Database Entry Fields for all Basic Model Listings (Entered by User)------Initial Database Entry Fields for all Basic Model Listings (Entered by User)-------Initial Database Entry Fields for all Basic Model Listings (Entered by User)--------Initial Database Entry Fields for all Basic Model Listings (Entered by User)
[6 empty] | nsp |  | MotorHP,NP | ηmotor,full,NP | S | Q100% | H100% | Q75% | H75% | Q110% | H110% | P75%in,M | P100%in,M | P110%in,M | P25%,in,C | P50%,in,C | P75%,in,C | P100%in,C
Method | Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | Rating Load Type | Configuration for which the pump is being rated | DOE Pump Category | If ST - Enter Bowl Diameter (in) | Nominal Speed of rotation | Is motor regulated under 10CFR 431.25? | Rated Motor Power used for default losses or Nameplate Rated Motor Power | For basic models distributed in commerce with a motor design under 10 CFR Part 431.25, Enter nominal nameplate motor efficiency. N/A for ST pumps and other non-regulated motors. All non ST pumps with motors not regulated under 10CFR 431.25, utilize Section III, Section IV, or Section VI as applicable | Number of Stages Tested | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Driver Power Input at 75% of BEP Rate of Flow (hp) | Driver Power Input at 100% of BEP Rate of Flow (hp) | Driver Power Input at 110% of BEP Rate of Flow (hp) | Measured control power input at 25% BEP target | Measured variable load control power input at 50% BEP target | Measured variable load control power input at 75% BEP target | Control Power Input at 100% of BEP Rate of Flow (hp) | PEICL | Basic Model Designation | Basic Model Full Impeller Diameter (in) | HI Approved Laboratory Registration Number
III | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve | Constant Load (CL) | Bare Pump | RSV | N/A | 3600 | No | 60 | N/A | 9 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 52.812 | 55.203 | 55.62 | N/A | N/A | N/A | N/A | 0.97 | xxx.xxx.xx | xxxxx | xxxx
IV | Section IV - Pump + Motor Tested Wire-to-Water Performance | Constant Load (CL) | Pump sold with motor | RSV | N/A | 3600 | No | 60 | N/A | 9 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 49.2013 | 51.4144 | 51.8084 | N/A | N/A | N/A | N/A | 0.9 | xxx.xxx.xx | xxxxx | xxxx
V | Section V - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor part Load Loss Curve | Constant Load (CL) | Pump sold with motor | ESCC | N/A | 3600 | Yes | 60 | 97 | 1 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 49.2013 | 51.4144 | 51.8084 | N/A | N/A | N/A | N/A | 0.78 | xxx.xxx.xx | xxxxx | xxxx
VI-a | Section VI - Pump + Motor + Control Tested Wire-to-Water Performance + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ST | 4 | 3600 | N/A | 60 | N/A | 9 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | N/A | N/A | N/A | 10 | 20 | 42 | 51.4144 | 0.47 | xxx.xxx.xx | xxxxx | xxxx
VI-b | Section VI - Pump + Motor + Control Tested Wire-to-Water Performance + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and non-continuous controls | ST | 4 | 3600 | N/A | 60 | N/A | 9 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | N/A | N/A | N/A | 10 | 20 | 42 | 51.4144 | 0.47 | xxx.xxx.xx | xxxxx | xxxx
VII | Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | Variable Load (VL) | Pump sold with motor and continuous controls | ESCC | N/A | 3600 | Yes | 60 | 97 | 1 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | N/A | N/A | N/A | 10 | 20 | 42 | 51.4144 | 0.47 | xxx.xxx.xx | xxxxx | xxxx
[5 empty] | Dependent on Cell E |  |  |  | Dependent on column H answer
Note on A7: Pete: Need to update this input sheet to be only what will be entered by the participant.

## Section III database
All database entry fields should be able to imported from any one of the calculation method tabs (Section III, Section IV, Section V, Section VI or Section VII. Note Secondary Fields differ by Section
Initial Database Entry Fields for all Basic Model Listings-------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings
[7 empty] | nsp |  | MotorHP or MotorHP,NP | Q100% | H100% | Q75% | H75% | Q110% | H110% |  | S |  | PEICL or PEIVL
Participant Company | Basic Model Designation | Rating Load Type | Configuration for which the pump is being rated | Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | DOE Pump Category | If ST Pump Bowl diameter (in) | Nominal Speed of rotation | DOE Equipment Category | Rated Motor Power used for default losses or Nameplate Rated Motor Power (MotorHP) | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Basic Model Full Impeller Diameter (in) | Number of Stages Tested | HI Approved Laboratory Registration Number | Enter PEI for Basic Model to be listed
xxxxx | xxx.xxx.xx | Constant Load (CL) | Bare Pump | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve | ESFM | N/A | 3600 | ESFM-3600 | 60 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | xxxxx | 9 | xxxx | 1.01
xxxxx | xxx.xxx.xx | Constant Load (CL) | Bare Pump | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve | RSV | N/A | 1800 | RSV-1800 | 125 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | xxxxx | 9 | xxxx | 1
xxxxx | xxx.xxx.xx | Constant Load (CL) | Bare Pump | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve | ST | 4 | 3600 | ST-3600 | 20 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | xxxxx | 9 | xxxx | 0.93
User enter - freeform entry | User Enter - Free form entered | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter -Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu | Calculation Combination of cells C & D | User dropdown | User enter - Freeform entry
| This is a unique designation for the product to be rated. Refer to 10 CFRxxxx |  |  | If CL is selected - Only sections III, IV and V are available If VL is selected - only section VI and VII are available | [13 empty] | Needs to communicate with HI PTLAP database to ensure it is a valid certificate number
P75%in,M | P100%in,M | P110%in,M | PERCL | PERSTD
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Calculate PERCL | PERSTD
52.812 | 55.203 | 55.62 | 54.5395 | 53.9995
52.812 | 55.203 | 55.62 | 54.5395 | 54.5395
49 | 51 | 52 | 50.6616 | 54.4748
|  |  | Calculation | Calculation
Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating----------------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating-----------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating
Ns | C |  | ηmotor,full | Lfull | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | CBaseline | ƞpump,Baseline | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Calculate Specifc Speed | Lookup Standard C-Value | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Caculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Standard | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
3741.6129 | 130.99 | ESFM-60-3600 | 93.6 | 4.1026 | 72.402 | 37.5325 | 33.0878 | 37.302 | 51.839 | 48.2578 | 52.3052 | 0.86398 | 0.8043 | 0.87175 | 0.90421 | 0.86261 | 0.90967 | 3.7096 | 3.5389 | 3.732 | 55.5486 | 51.7967 | 56.0372 | 54.4554 | 136.59 | 66.802 | 56.1846 | 52.3033 | 56.69 | 0.93641 | 0.87172 | 0.94483 | 0.95532 | 0.90965 | 0.96127 | 3.9193 | 3.7319 | 3.9437 | 60.1039 | 56.0352 | 60.6336 | 58.9183 | 1.082 | 7.1956 | 0.99163
1870.8064 | 130.99 | RSV-125-1800 | 93.6 | 8.547 | 72.402 | 37.5325 | 33.0878 | 37.302 | 51.839 | 48.2578 | 52.3052 | 0.86398 | 0.8043 | 0.87175 | 0.90421 | 0.86261 | 0.90967 | 3.7096 | 3.5389 | 3.732 | 55.5486 | 51.7967 | 56.0372 | 54.4554 | 136.59 | 66.802 | 56.1846 | 52.3033 | 56.69 | 0.93641 | 0.87172 | 0.94483 | 0.95532 | 0.90965 | 0.96127 | 3.9193 | 3.7319 | 3.9437 | 60.1039 | 56.0352 | 60.6336 | 58.9183 | 1.082 | 8.1956 | 1.0015
3741.6129 | 130.99 | ST-20-3600 | 93.6 | 1.3675 | 72.402 | 37.5325 | 33.0878 | 37.302 | 51.839 | 48.2578 | 52.3052 | 0.86398 | 0.8043 | 0.87175 | 0.90421 | 0.86261 | 0.90967 | 3.7096 | 3.5389 | 3.732 | 55.5486 | 51.7967 | 56.0372 | 54.4554 | 136.59 | 66.802 | 56.1846 | 52.3033 | 56.69 | 0.93641 | 0.87172 | 0.94483 | 0.95532 | 0.90965 | 0.96127 | 3.9193 | 3.7319 | 3.9437 | 60.1039 | 56.0352 | 60.6336 | 58.9183 | 1.082 | 15.1956 | 1.0004
calculation | Lookup | Calculation Combination of cells C, L & D for later lookup | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation
| CBaseline |  |  |  | ƞpump,Baseline |  |  |  | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERBaseline
| Lookup baseline C-Value |  |  |  | Calculate baseline pump Efficiency |  |  |  | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Baseline
-777.0583
104.2626
1479.2635
-686.59
#REF!
Note on D14: Scott Frees: Divided by 3, instead of multiplying by 0.3333 to avoid rounding errors

## Section IV database
All database entry fields should be able to imported from any one of the calculation method tabs (Section III, Section IV, Section V, Section VI or Section VII. Note Secondary Fields differ by Section
Initial Database Entry Fields for all Basic Model Listings-------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings
[7 empty] | nsp |  | ηmotor,full,NP |  | MotorHP or MotorHP,NP |  | Q100% | H100% | Q75% | H75% | Q110% | H110% |  | S |  | PEICL or PEIVL
Participant Company | Basic Model Designation | Rating Load Type | Configuration for which the pump is being rated | Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | DOE Pump Category | If ST Pump Bowl diameter (in) | Nominal Speed of rotation | Is Motor Regulated under 10 CFR 431.25 | If regulated under 10 CFR 431.25 - Nominal Motor Efficiency | DOE Equipment Category | Rated Motor Power used for default losses or Nameplate Rated Motor Power (MotorHP) | MotorHP and Speed | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Basic Model Full Impeller Diameter (in) | Number of Stages Tested | HI Approved Laboratory Registration Number | Enter PEI for Basic Model to be listed
xxxxx | xxx.xxx.xx | Constant Load (CL) | Pump sold with motor | Section IV - Pump + Motor Tested Wire-to-Water Performance | RSV | N/A | 3600 | no | N/A | RSV-3600 | 60 | 60-3600 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | xxxxx | 9 | xxxx | 0.9
User enter - freeform entry | User Enter - Free form entered | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter -Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu |  |  | Calculation Combination of cells C & D | User dropdown | Calculation Combination of cells L & D | User enter - Freeform entry
| This is a unique designation for the product to be rated. Refer to 10 CFRxxxx |  |  | If CL is selected - Only sections III, IV and V are available If VL is selected - only section VI and VII are available | [16 empty] | Needs to communicate with HI PTLAP database to ensure it is a valid certificate number
If PEI Calculation Methods Section
P75%in,M | P100%in,M | P110%in,M | PERCL | PERSTD
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Calculate PERCL | PERSTD
49.2013 | 51.4144 | 51.8084 | 50.8029 | 56.4477
|  |  | Calculation | Calculation
Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating----------------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating-----------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating
Ns | C |  | ηmotor,full | Lfull | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | CBaseline | ƞpump,Baseline | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Calculate Specifc Speed | Lookup Standard C-Value | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Caculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Standard | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
3741.6129 | 133.2 | RSV-60-3600 | 93.6 | 4.1026 | 70.192 | 37.5325 | 33.0878 | 37.302 | 53.4711 | 49.7772 | 53.9521 | 0.89119 | 0.82962 | 0.8992 | 0.92337 | 0.88016 | 0.92903 | 3.7882 | 3.6109 | 3.8114 | 57.2593 | 53.3881 | 57.7635 | 56.1314 | 133.2 | 70.192 | 53.4711 | 49.7772 | 53.9521 | 0.89119 | 0.82962 | 0.8992 | 0.92337 | 0.88016 | 0.92903 | 3.7882 | 3.6109 | 3.8114 | 57.2593 | 53.3881 | 57.7635 | 56.1314 | 1 | 10 | 1.0056
calculation | Lookup | Calculation Combination of cells C, L & D for later lookup | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation
5.8574
8.2273
#REF!

## Section V database
All database entry fields should be able to imported from any one of the calculation method tabs (Section III, Section IV, Section V, Section VI or Section VII. Note Secondary Fields differ by Section
Initial Database Entry Fields for all Basic Model Listings-------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings
[7 empty] | nsp |  | ηmotor,full,NP |  | MotorHP or MotorHP,NP |  | Q100% | H100% | Q75% | H75% | Q110% | H110% |  | S |  | PEICL or PEIVL
Participant Company | Basic Model Designation | Rating Load Type | Configuration for which the pump is being rated | Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | DOE Pump Category | If ST - Bowl diameter (in) | Nominal Speed of rotation | Is Motor Regulated under 10 CFR 431.25 | If regulated under 10 CFR 431.25 - Nominal Motor Efficiency | DOE Equipment Category | Rated Motor Power used for default losses or Nameplate Rated Motor Power (MotorHP) | MotorHP and Speed | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Basic Model Full Impeller Diameter (in) | Number of Stages Tested | HI Approved Laboratory Registration Number | Enter PEI for Basic Model to be listed
xxxxx | xxx.xxx.xx | Constant Load (CL) | Pump sold with motor | Section V - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor part Load Loss Curve | ESCC | N/A | 3600 | Yes | 97 | ESCC-3600 | 60 | 60-3600 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | xxxxx | 1 | xxxx | 0.78
User enter - freeform entry | User Enter - Free form entered | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter -Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu |  |  | Calculation Combination of cells C & D | User dropdown | Calculation Combination of cells L & D | User enter - Freeform entry
| This is a unique designation for the product to be rated. Refer to 10 CFRxxxx |  |  | If CL is selected - Only sections III, IV and V are available If VL is selected - only section VI and VII are available | [16 empty] | Needs to communicate with HI PTLAP database to ensure it is a valid certificate number
If PEI Calculation Methods Section
P75%in,M | P100%in,M | P110%in,M | PERCL | PERSTD
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Calculate PERCL | PERSTD
49.2013 | 51.4144 | 51.8084 | 50.8029 | 65.1319
|  |  | Calculation | Calculation
Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating----------------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating-----------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating
Ns | C |  | ηmotor,full | Lfull | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | CBaseline | ƞpump,Baseline | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Calculate Specifc Speed | Lookup Standard C-Value | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Caculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Standard | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
720.0737 | 130.42 | ESCC-60-3600 | 93.6 | 4.1026 | 60.4576 | 37.5325 | 33.0878 | 37.302 | 62.0807 | 57.792 | 62.6391 | 1 | 0.9632 | 1 | 1 | 0.97421 | 1 | 4.1026 | 3.9968 | 4.1026 | 66.1833 | 61.7888 | 66.7416 | 64.8981 | 135.94 | 54.9376 | 68.3184 | 63.5988 | 68.9329 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1026 | 4.1026 | 4.1026 | 72.421 | 67.7014 | 73.0355 | 71.0455 | 1.0947 | 31.4725 | 1.0036
calculation | Lookup | Calculation Combination of cells C, L & D for later lookup | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation
|  |  | 60.4576 | 60.4576 | 5.8574
|  |  | -686.02 | -686.02 | 6.5794
|  |  | 1182.9678 | 1182.9678
|  |  | 104.2626 | 104.2626
|  |  | -496.945 | -496.945
|  |  | -14.6445 | -14.6445
|  |  | -29.1633 | -29.1633 | [18 empty] | #REF!

## Section VI database
All database entry fields should be able to imported from any one of the calculation method tabs (Section III, Section IV, Section V, Section VI or Section VII. Note Secondary Fields differ by Section
Initial Database Entry Fields for all Basic Model Listings-------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings
[7 empty] | nsp |  | ηmotor,full,NP |  | MotorHP or MotorHP,NP |  | Q100% | H100% | Q75% | H75% | Q110% | H110% |  | S |  | PEICL or PEIVL
Participant Company | Basic Model Designation | Rating Load Type | Configuration for which the pump is being rated | Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | DOE Pump Category | If ST - Bowl diameter (in) | Nominal Speed of rotation | Is Motor Regulated under 10 CFR 431.25 | If regulated under 10 CFR 431.25 - Nominal Motor Efficiency | DOE Equipment Category | Rated Motor Power used for default losses or Nameplate Rated Motor Power (MotorHP) | MotorHP and Speed | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Basic Model Full Impeller Diameter (in) | Number of Stages Tested | HI Approved Laboratory Registration Number | Enter PEI for Basic Model to be listed
xxxxx | xxx.xxx.xx | Variable Load (VL) | Pump sold with motor and continuous controls | Section VI - Pump + Motor + Control Tested Wire-to-Water Performance + Assumed Control Curve | ST | 4 | 3600 | N/A | N/A | ST-3600 | 60 | 60-3600 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | xxxxx | 9 | xxxx | 0.47
[6 empty] | 101.6 |  |  |  |  | 44.742 |  | 79.4552 | 129.3662 | 59.5914 | 152.062 | 87.4007 | 116.8835
User enter - freeform entry | User Enter - Free form entered | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter -Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu |  |  | Calculation Combination of cells C & D | User dropdown | Calculation Combination of cells L & D | User enter - Freeform entry
| This is a unique designation for the product to be rated. Refer to 10 CFRxxxx |  |  | If CL is selected - Only sections III, IV and V are available If VL is selected - only section VI and VII are available | [16 empty] | Needs to communicate with HI PTLAP database to ensure it is a valid certificate number
P25%in,C | P50%in,C | P75%in,C | P100%in,C | PERCL | PERSTD
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Bowl diameter (in) | Calculate PERCL | PERSTD
10 | 20 | 42 | 51.4144 | 30.8536 | 65.6459
7.457 | 14.914 | 31.3194 | 38.3397 | Calculation | Calculation
Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating----------------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating-----------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating
Ns | C |  | ηmotor,full | Lfull | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | CBaseline | ƞpump,Baseline | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Calculate Specifc Speed | Lookup Standard C-Value | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Caculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Standard | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
3741.6129 | 134.85 | ST-60-3600 | 81.5 | 13.6196 | 68.542 | 37.5325 | 33.0878 | 37.302 | 54.7583 | 50.9755 | 55.2509 | 0.91264 | 0.84959 | 0.92085 | 0.93853 | 0.89411 | 0.94433 | 12.7824 | 12.1774 | 12.8614 | 67.5407 | 63.1529 | 68.1122 | 66.262 | 138.78 | 64.612 | 58.089 | 54.0761 | 58.6115 | 0.96815 | 0.90127 | 0.97686 | 0.97769 | 0.93049 | 0.98381 | 13.3158 | 12.6729 | 13.3991 | 71.4048 | 66.749 | 72.0106 | 70.0478 | 1.0571 | 58.7134 | 0.9907
calculation | Lookup | Calculation Combination of cells C, L & D for later lookup | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation
#REF!

## Section VII database
All database entry fields should be able to imported from any one of the calculation method tabs (Section III, Section IV, Section V, Section VI or Section VII. Note Secondary Fields differ by Section
Initial Database Entry Fields for all Basic Model Listings-------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings
[7 empty] | nsp |  | ηmotor,full,NP |  | MotorHP or MotorHP,NP |  | Q100% | H100% | Q75% | H75% | Q110% | H110% |  | S |  | PEICL or PEIVL
Participant Company | Basic Model Designation | Rating Load Type | Configuration for which the pump is being rated | Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | DOE Pump Category | If ST - Bowl diameter (in) | Nominal Speed of rotation | Is Motor Regulated under 10 CFR 431.25 | If regulated under 10 CFR 431.25 - Nominal Motor Efficiency | DOE Equipment Category | Rated Motor Power used for default losses or Nameplate Rated Motor Power (MotorHP) | MotorHP and Speed | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Basic Model Full Impeller Diameter (in) | Number of Stages Tested | HI Approved Laboratory Registration Number | Enter PEI for Basic Model to be listed
xxxxx | xxxxx | Variable Load (VL) | Pump sold with motor and continuous controls | Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve | ESCC | N/A | 3600 | Yes | 97 | ESCC-3600 | 60 | 60-3600 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | xxxxx | 1 | xxxx | 0.47
User enter - freeform entry | User Enter - Free form entered | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter -Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu |  |  | Calculation Combination of cells C & D | User dropdown | Calculation Combination of cells L & D | User enter - Freeform entry
| This is a unique designation for the product to be rated. Refer to 10 CFRxxxx |  |  | If CL is selected - Only sections III, IV and V are available If VL is selected - only section VI and VII are available | [16 empty] | Needs to communicate with HI PTLAP database to ensure it is a valid certificate number
P25%in,C | P50%in,C | P75%in,C | P100%in,C | PERCL | PERSTD
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Bowl diameter (in) | Calculate PERCL | PERSTD
10 | 20 | 42 | 51.4144 | 30.8536 | 65.6459
|  |  | User Enter - Dropdown menu | Calculation | Calculation
Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating----------------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating-----------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating
Ns | C |  | ηmotor,full | Lfull | ƞpump,STD | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | X100%STD | X75%STD | X110%STD | Y100%STD | Y75%STD | Y110%STD | L100%STD | L75%STD | L110%STD | P100%in,STD | P75%in,STD | P110%in,STD | PERSTD | CBaseline | ƞpump,Baseline | P100%Baseline | P75%Baseline | P110%Baseline | X100%Baseline | X75%Baseline | X110%Baseline | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Calculate Specifc Speed | Lookup Standard C-Value | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Caculate Std pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Standard | Lookup baseline C-Value | Calculate baseline pump Efficiency | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
720.0737 | 130.42 | ESCC-60-3600 | 93.6 | 4.1026 | 60.4576 | 37.5325 | 33.0878 | 37.302 | 62.0807 | 57.792 | 62.6391 | 1 | 0.9632 | 1 | 1 | 0.97421 | 1 | 4.1026 | 3.9968 | 4.1026 | 66.1833 | 61.7888 | 66.7416 | 64.8981 | 135.94 | 54.9376 | 68.3184 | 63.5988 | 68.9329 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1026 | 4.1026 | 4.1026 | 72.421 | 67.7014 | 73.0355 | 71.0455 | 1.0947 | 62.4725 | 1.0115
calculation | Lookup | Calculation Combination for lookup | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation
#REF!

## ER cert A.1 to B.1
Section III to Section IV Energy Rating Certificate Calcualtion --- Regualted Motor Added to HI ER Rated Bare Pump------------------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calcualtion --- Regualted Motor Added to HI ER Rated Bare Pump-----------------------------------------------------------Section III to Section IV Energy Rating Certificate Calcualtion --- Regualted Motor Added to HI ER Rated Bare Pump-----------------------------------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calcualtion --- Regualted Motor Added to HI ER Rated Bare Pump--------------------Section III to Section IV Energy Rating Certificate Calcualtion --- Regualted Motor Added to HI ER Rated Bare Pump
[8 empty] | (MotorHP,NP) | (ηmotor,full,NP) | nsp |  | S | PEICL | (MotorHP) |  | ηmotor,full,certificate | Q100% | H100% | Q75% | H75% | Q110% | H110% | P75%in,M | (P100%in,M) | P110%in,M | PERCL | PERSTD | Lfull | X75% | X100% | X110% | Y75% | Y100% | Y110% | L75% | L100% | L110% | P75% | P100% | P110% | X75%NP | X100%NP | X110%NP | Y75%NP | Y100%NP | Y110%NP | LfullNP | L75%NP | L100%NP | L110%NP | P75%in,M,Certificate | P100%in,M,Certificate | P110%in,M,Certificate | PERCLCertificate | PEICLCertificate | P75%Baseline | P100%Baseline | P110%Baseline | X75%Baseline | X100%Baseline | X110%Baseline | Y75%Baseline | Y100%Baseline | Y110%Baseline | LfullCertificate | L75%Baseline | L100%Baseline | L110%Baseline | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Pump Manufacturer | Basic model designation | Look up original test method | Are you adding a regualted motor? | Are you adding a variable speed drive | Calculation method, based on previous two answers | Manufacturer of Motor added | Model number of motor added | Rated power of motor added (MotorHPNP) | Efficiency of motor added (ηmotor,full,NP) | Look up Nominal speed of rotation (nsp) | Lookup DOE equipment category | Lookup Number of Stages | Lookup PEICL | Look up Motor power used for default losses (MotorHP) | Certificate equipment class and MotorHP | Lookup default motor efficiency of motor added | Lookup Flow at BEP | Lookup Head at BEP | Lookup Flow at 75% BEP | Lookup Head at 75% BEP | Lookup Flow at 110% BEP | Lookup Head at 110% BEP | Look up driver power input at 75% BEP | Lookup driver power input at 100% BEP | Look up driver power input at 110% BEP | calculate PERCL | Calculate PERSTD | Calculate Standard (default) Full Load Motor Losses | motor power ratio at 75% BEP | motor power ratio at 100% BEP | motor power ratio at 110% BEP | Part Load Loss Factor at 75% BEP | Part Load Loss Factor at 100% BEP | Part Load Loss Factor at 110% BEP | Calculate part load loss at 75% BEP | Calculate part load loss at 100% BEP | Calculate part load loss at 110% BEP | Calculate pump input power at 75% BEP | Calculate pump input power at 100% BEP | Calculate pump input power at 110% BEP | nameplate motor power ratio at 75% BEP | nameplate motor power ratio at 100% BEP | nameplate motor power ratio at 110% BEP | nameplate Part Load Loss Factor at 75% BEP | nameplate Part Load Loss Factor at 100% BEP | nameplate Part Load Loss Factor at 110% BEP | Cacluate nameplate full load motor losses | Calculate nameplate part load loss at 75% BEP | Calculate nameplate part load loss at 100% BEP | Calculate nameplate part load loss at 110% BEP | Calculate driver input power to the certificate product at 75% BEP | Calculate driver input power to the Certificate product at 100% BEP | Calculate driver input power to the certificate product at 110% BEP | Calculate constant load pump energy rating for certificate | Calculate constant load pump energy index for certificate | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 110% BEP | Calculate baseline motor losses for Extended Product MotorHP | Baseline part load losses at 75% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
xxxxxx | xxxx | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve | Y | N | Section III to Section V - Rated Bare Pump + Regulated Extended Motor (Constant Load) | xxxx | xxxx | 50 | 97 | 3600 | ESFM | 9 | 1.01 | 60 | ESFM-50-3600 | 93 | 349.8305 | 424.4298 | 262.3729 | 498.8911 | 384.8136 | 383.476 | 52.812 | 55.203 | 55.62 | 54.5395 | 53.9995 | 4.1026 | 0.82387 | 0.86117 | 0.86767 | 0.87616 | 0.90223 | 0.9068 | 3.5945 | 3.7015 | 3.7202 | 49.2175 | 51.5015 | 51.8998 | 0.98435 | 1 | 1 | 0.98906 | 1 | 1 | 1.5464 | 1.5295 | 1.5464 | 1.5464 | 50.747 | 53.0479 | 53.4462 | 52.4085 | 0.97054 | 52.3033 | 56.1846 | 56.69 | 1 | 1 | 1 | 1 | 1 | 1 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 59.9481 | 56.0667 | 60.4534 | 58.8168 | 1.0892 | 11.8675
Drop down of participants in program | Drop down of basic models listed by participant | database lookup |  |  | Based on First two answers | free form entry | free form entry | Free form entry | free form entry | database lookup | database lookup | database lookup | database lookup | database lookup | calculation for standard lookup | Standard lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | database lookup | database lookup | database lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation

## ER cert A.1_B.1_C.1
Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump---------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump-------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump----------------------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump--------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump
[8 empty] | (MotorHP,NP) | (ηmotor,full,NP) |  |  | nsp |  | S | PEICL | (MotorHP) |  | ηmotor,full,certificate | Q100% | H100% | (P100%in,M) | PERCL | PERSTD | Lfull | X100% | Y100% | L100% | P100% | P75%VL | P50%VL | P25%VL | X100%NP | X75%NP | X50%NP | X25%NP | a | b | c | Z100% | Z75% | Z50% | Z25% | LfullNP | L100%M,C | L75%M,C | L50%M,C | L25%M,C | P100%in,C | P75%in,C | P50%in,C | P25%in,C | PERVLCertificate | PEIVLCertificate | P75%Baseline | P100%Baseline | P110%Baseline | X75%Baseline,Certificate | X100%Baseline,Certificate | X110%Baseline,Certificate | Y75%Baseline,Certificate | Y100%Baseline,Certificate | Y110%Baseline,Certificate | LfullCertificate | L75%Baseline | L100%Baseline | L110%Baseline | P75%in,Baseline | P100%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Pump Manufacturer | Basic model designation | Look up original test method | Are you adding a regulated motor? | Are you adding a variable speed drive | Calculation method, based on previous two answers | Manufacturer of Motor added | Model number of motor added | Rated power of motor added (MotorHPNP) | Efficiency of motor added (ηmotor,full,NP) | Manufacturer of continuous control added | Model number of continuous Control Added | Look up Nominal speed of rotation (nsp) | Lookup DOE equipment category | Lookup Number of Stages | Lookup PEICL | Look up Motor power used for default losses (MotorHP) | Certificate equipment class and MotorHP | Lookup default motor efficiency of motor added | Lookup Flow at BEP | Lookup Head at BEP | Lookup driver power input at 100% BEP | calculate PERCL | Calculate PERSTD | Calculate Standard (default) Full Load Motor Losses | motor power ratio at 100% BEP | Part Load Loss Factor at 100% BEP | Calculate part load loss at 100% BEP | Calculate pump input power at 100% BEP | Calculate pump input power at 75% BEP | Calculate pump input power at 50% BEP | Calculate pump input power at 25% BEP | nameplate motor power ratio at 100% BEP | nameplate motor power ratio at 75% BEP | nameplate motor power ratio at 50% BEP | nameplate motor power ratio at 25% BEP | Look up "a" coefficient | Look up "b" coefficient | Look up "c" coefficient | Motor & control Part Load Loss Factor at 100% BEP | Motor & control Part Load Loss Factor at 75% BEP | Motor & control Part Load Loss Factor at 50% BEP | Motor & control Part Load Loss Factor at 25% BEP | Calculate nameplate full load motor losses | Calculate motor & control part load loss at 100% BEP | Calculate motor & control part load loss at 75% BEP | Calculate motor & control part load loss at 50% BEP | Calculate motor & control part load loss at 25% BEP | Calculate control input power to the Certificate product at 100% BEP | Calculate control input power to the Certificate product at 75% BEP | Calculate control input power to the Certificate product at 50% BEP | Calculate control input power to the Certificate product at 25% BEP | Calculate constant load pump energy rating for certificate | Calculate constant load pump energy index for certificate | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 110% BEP | Calculate baseline motor losses for Extended Product MotorHP | Baseline part load losses at 75% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
xxxxxx | xxxx | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve | Y | Y | Section III to Section V to Section VII - Rated Bare Pump + Regulated Extended Motor + Continuous Control (Variable Load) | xxxx | xxxx | 50 | 97 | xxxx | xxxx | 3600 | ESFM | 9 | 1.01 | 60 | ESFM-50-3600 | 93 | 349.8305 | 424.4298 | 55.203 | 54.5395 | 53.9995 | 4.1026 | 0.86117 | 0.90223 | 3.7015 | 51.5015 | 25.107 | 10.3003 | 3.2188 | 1 | 0.50214 | 0.20601 | 0.064377 | -1.5122 | 3.0777 | 0.1847 | 1.7502 | 1.3488 | 0.75455 | 0.37657 | 1.5464 | 2.7065 | 2.0858 | 1.1668 | 0.58232 | 54.208 | 27.1928 | 11.4671 | 3.8012 | 24.1673 | 0.44755 | 52.3033 | 56.1846 | 56.69 | 1 | 1 | 1 | 1 | 1 | 1 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 56.0667 | 59.9481 | 60.4534 | 58.8168 | 1.0892 | 64.1664
Drop down of participants in program | Drop down of basic models listed by participant | database lookup |  |  | Based on First two answers | free form entry | free form entry | Free form entry | free form entry |  | free form entry | database lookup | database lookup | database lookup | database lookup | database lookup | calculation for standard lookup | Standard lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Standard Look up | Standard Look up | Standard Look up | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation |  | Calculation | Calculation | Calculation | database lookup | database lookup | database lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation

## ER cert A.1_C.1
Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump---------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump-------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump----------------------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump--------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump
[8 empty] | (MotorHP,NP) |  |  | nsp |  | S | PEICL | (MotorHP) |  | ηmotor,full,certificate | Q100% | H100% | (P100%in,M) | PERCL | PERSTD | Lfull | X100% | Y100% | L100% | P100% | P75%VL | P50%VL | P25%VL | X100%NP | X75%NP | X50%NP | X25%NP | a | b | c | Z100% | Z75% | Z50% | Z25% | LfullNP | L100%M,C | L75%M,C | L50%M,C | L25%M,C | P100%in,C | P75%in,C | P50%in,C | P25%in,C | PERVLCertificate | PEIVLCertificate | P75%Baseline | P100%Baseline | P110%Baseline | X75%Baseline,Certificate | X100%Baseline,Certificate | X110%Baseline,Certificate | Y75%Baseline,Certificate | Y100%Baseline,Certificate | Y110%Baseline,Certificate | LfullCertificate | L75%Baseline | L100%Baseline | L110%Baseline | P75%in,Baseline | P100%in,Baseline | P110%in,Baseline | PERBaseline | PEIBaseline | ER
Pump Manufacturer | Basic model designation | Look up original test method | Are you adding a regulated motor? | Are you adding a variable speed drive | Calculation method, based on previous two answers | Manufacturer of Motor added | Model number of motor added | Rated power of motor added (MotorHPNP) | Manufacturer of continuous control added | Model number of continuous Control Added | Look up Nominal speed of rotation (nsp) | Lookup DOE equipment category | Lookup Number of Stages | Lookup PEICL | Look up Motor power used for default losses (MotorHP) | Certificate equipment class and MotorHP | Lookup default motor efficiency of motor added | Lookup Flow at BEP | Lookup Head at BEP | Lookup driver power input at 100% BEP | calculate PERCL | Calculate PERSTD | Calculate Standard (default) Full Load Motor Losses | motor power ratio at 100% BEP | Part Load Loss Factor at 100% BEP | Calculate part load loss at 100% BEP | Calculate pump input power at 100% BEP | Calculate pump input power at 75% BEP | Calculate pump input power at 50% BEP | Calculate pump input power at 25% BEP | nameplate motor power ratio at 100% BEP | nameplate motor power ratio at 75% BEP | nameplate motor power ratio at 50% BEP | nameplate motor power ratio at 25% BEP | Look up "a" coefficient | Look up "b" coefficient | Look up "c" coefficient | Motor & control Part Load Loss Factor at 100% BEP | Motor & control Part Load Loss Factor at 75% BEP | Motor & control Part Load Loss Factor at 50% BEP | Motor & control Part Load Loss Factor at 25% BEP | Calculate nameplate full load motor losses | Calculate motor & control part load loss at 100% BEP | Calculate motor & control part load loss at 75% BEP | Calculate motor & control part load loss at 50% BEP | Calculate motor & control part load loss at 25% BEP | Calculate control input power to the Certificate product at 100% BEP | Calculate control input power to the Certificate product at 75% BEP | Calculate control input power to the Certificate product at 50% BEP | Calculate control input power to the Certificate product at 25% BEP | Calculate constant load pump energy rating for certificate | Calculate constant load pump energy index for certificate | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 110% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 110% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 110% BEP | Calculate baseline motor losses for Extended Product MotorHP | Baseline part load losses at 75% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 110% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 110% BEP | Calculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
xxxxxx | xxxx | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve | N | Y | Section III to Section V to Section VII - Rated Bare Pump + Extended Motor + Continuous Control (Variable Load) | xxxx | xxxx | 50 | xxxx | xxxx | 3600 | ESFM | 9 | 1.01 | 60 | ESFM-50-3600 | 93 | 349.8305 | 424.4298 | 55.203 | 54.5395 | 53.9995 | 4.1026 | 0.86117 | 0.90223 | 3.7015 | 51.5015 | 25.107 | 10.3003 | 3.2188 | 1 | 0.50214 | 0.20601 | 0.064377 | -1.5122 | 3.0777 | 0.1847 | 1.7502 | 1.3488 | 0.75455 | 0.37657 | 3.7634 | 6.5868 | 5.0763 | 2.8397 | 1.4172 | 58.0883 | 30.1833 | 13.14 | 4.636 | 26.5119 | 0.49097 | 52.3033 | 56.1846 | 56.69 | 1 | 1 | 1 | 1 | 1 | 1 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 56.0667 | 59.9481 | 60.4534 | 58.8168 | 1.0892 | 59.8245
Drop down of participants in program | Drop down of basic models listed by participant | database lookup |  |  | Based on First two answers | free form entry | free form entry | Free form entry |  | free form entry | database lookup | database lookup | database lookup | database lookup | database lookup | calculation for standard lookup | Standard lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Standard Look up | Standard Look up | Standard Look up | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation |  | Calculation | Calculation | Calculation | database lookup | database lookup | database lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation

## ER cert B.1_C.1
Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump---------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump-------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump----------------------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump--------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump
[8 empty] | nsp |  | PEICL | (MotorHP,NP) | ηmotor,full,NP | Q100% | H100% | (P100%in,M) | PERCL | PERSTD | Lfull | X100% | Y100% | L100% | P100% | P75%VL | P50%VL | P25%VL | X100%NP | X75%NP | X50%NP | X25%NP | a | b | c | Z100% | Z75% | Z50% | Z25% | LfullNP | L100%M,C | L75%M,C | L50%M,C | L25%M,C | P100%in,C | P75%in,C | P50%in,C | P25%in,C | PERVLCertificate | PEIVLCertificate | PEIBaseline | ER
Pump Manufacturer | Basic model designation | Look up original test method | Are you adding a regulated motor? | Are you adding a variable speed drive | Calculation method, based on previous two answers | Manufacturer of continuous control added | Model number of continuous Control Added | Look up Nominal speed of rotation (nsp) | Lookup DOE equipment category | Lookup PEICL | Look up nameplate Motor power used for default losses (MotorHP) | look up ηmotor,full,NP | Lookup Flow at BEP | Lookup Head at BEP | Lookup driver power input at 100% BEP | calculate PERCL | Calculate PERSTD | Calculate Standard (default) Full Load Motor Losses | motor power ratio at 100% BEP | Part Load Loss Factor at 100% BEP | Calculate part load loss at 100% BEP | Calculate pump input power at 100% BEP | Calculate pump input power at 75% BEP | Calculate pump input power at 50% BEP | Calculate pump input power at 25% BEP | nameplate motor power ratio at 100% BEP | nameplate motor power ratio at 75% BEP | nameplate motor power ratio at 50% BEP | nameplate motor power ratio at 25% BEP | Look up "a" coefficient | Look up "b" coefficient | Look up "c" coefficient | Motor & control Part Load Loss Factor at 100% BEP | Motor & control Part Load Loss Factor at 75% BEP | Motor & control Part Load Loss Factor at 50% BEP | Motor & control Part Load Loss Factor at 25% BEP | Calculate nameplate full load motor losses | Calculate motor & control part load loss at 100% BEP | Calculate motor & control part load loss at 75% BEP | Calculate motor & control part load loss at 50% BEP | Calculate motor & control part load loss at 25% BEP | Calculate control input power to the Certificate product at 100% BEP | Calculate control input power to the Certificate product at 75% BEP | Calculate control input power to the Certificate product at 50% BEP | Calculate control input power to the Certificate product at 25% BEP | Calculate constant load pump energy rating for certificate | Calculate constant load pump energy index for certificate | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
xxxxxx | xxxx | Section V - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor part Load Loss Curve | N/A | Y | Section V to Section VII - Rated Bare Pump + Regulated Motor + Extended Continuous Control (Variable Load) | xxxx | xxxx | 3600 | ESCC | 0.78 | 60 | 97 | 349.8305 | 424.4298 | 51.4144 | 50.8029 | 65.1319 | 4.1026 | 0.80206 | 0.86107 | 3.5326 | 47.8818 | 23.3424 | 9.5764 | 2.9926 | 0.79803 | 0.38904 | 0.15961 | 0.049877 | -0.8914 | 2.8846 | 0.2625 | 1.9968 | 1.2498 | 0.70019 | 0.40416 | 1.8557 | 3.7054 | 2.3192 | 1.2993 | 0.74998 | 51.5872 | 25.6616 | 10.8757 | 3.7426 | 22.9668 | 0.35262 | 1.0947 | 74.2105
Drop down of participants in program | Drop down of basic models listed by participant | database lookup |  |  | Based on First two answers |  | free form entry | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Standard Look up | Standard Look up | Standard Look up | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | database lookup | Calculation

## ER cert B.2_C.1
Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump---------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump-------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump----------------------------------------------------------------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump--------------------Section III to Section IV Energy Rating Certificate Calculation --- Regulated Motor Added to HI ER Rated Bare Pump
[8 empty] | nsp |  | PEICL | (MotorHP,NP) | ηmotor,full or ηmotor,full,NP | Q100% | H100% | (P100%in,M) | PERCL | PERSTD | Lfull | X100% | Y100% | L100% | P100% | P75%VL | P50%VL | P25%VL | X100%NP | X75%NP | X50%NP | X25%NP | a | b | c | Z100% | Z75% | Z50% | Z25% | LfullNP | L100%M,C | L75%M,C | L50%M,C | L25%M,C | P100%in,C | P75%in,C | P50%in,C | P25%in,C | PERVLCertificate | PEIVLCertificate | PEIBaseline | ER
Pump Manufacturer | Basic model designation | Look up original test method | Are you adding a regulated motor? | Are you adding a variable speed drive | Calculation method, based on previous two answers | Manufacturer of continuous control added | Model number of continuous Control Added | Look up Nominal speed of rotation (nsp) | Lookup DOE equipment category | Lookup PEICL | Look up nameplate Motor power used for default losses (MotorHP) | ηmotor,full | Lookup Flow at BEP | Lookup Head at BEP | Lookup driver power input at 100% BEP | calculate PERCL | Calculate PERSTD | Calculate Standard (default) Full Load Motor Losses | motor power ratio at 100% BEP | Part Load Loss Factor at 100% BEP | Calculate part load loss at 100% BEP | Calculate pump input power at 100% BEP | Calculate pump input power at 75% BEP | Calculate pump input power at 50% BEP | Calculate pump input power at 25% BEP | nameplate motor power ratio at 100% BEP | nameplate motor power ratio at 75% BEP | nameplate motor power ratio at 50% BEP | nameplate motor power ratio at 25% BEP | Look up "a" coefficient | Look up "b" coefficient | Look up "c" coefficient | Motor & control Part Load Loss Factor at 100% BEP | Motor & control Part Load Loss Factor at 75% BEP | Motor & control Part Load Loss Factor at 50% BEP | Motor & control Part Load Loss Factor at 25% BEP | Calculate nameplate full load motor losses | Calculate motor & control part load loss at 100% BEP | Calculate motor & control part load loss at 75% BEP | Calculate motor & control part load loss at 50% BEP | Calculate motor & control part load loss at 25% BEP | Calculate control input power to the Certificate product at 100% BEP | Calculate control input power to the Certificate product at 75% BEP | Calculate control input power to the Certificate product at 50% BEP | Calculate control input power to the Certificate product at 25% BEP | Calculate constant load pump energy rating for certificate | Calculate constant load pump energy index for certificate | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
xxxxxx | xxxx | Section IV - Pump + Motor Tested Wire-to-Water Performance | N/A | Y | Section V to Section VII - Rated Bare Pump + Regulated or unregulated Motor + Extended Continuous Control (Variable Load) | xxxx | xxxx | 3600 | RSV | 0.9 | 60 | 93.6 | 349.8305 | 424.4298 | 51.4144 | 50.8029 | 56.4477 | 4.1026 | 0.80206 | 0.86107 | 3.5326 | 47.8818 | 23.3424 | 9.5764 | 2.9926 | 0.79803 | 0.38904 | 0.15961 | 0.049877 | -0.8914 | 2.8846 | 0.2625 | 1.9968 | 1.2498 | 0.70019 | 0.40416 | 4.1026 | 8.192 | 5.1274 | 2.8726 | 1.6581 | 56.0738 | 28.4698 | 12.4489 | 4.6507 | 25.4108 | 0.45017 | 1 | 54.9834
Drop down of participants in program | Drop down of basic models listed by participant | database lookup |  |  | Based on First two answers |  | free form entry | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | database lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Standard Look up | Standard Look up | Standard Look up | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | database lookup | Calculation

## Lookup
Bare Pump
Pump sold with motor
Pump sold with motor and continuous controls
Pump sold with motor and non-continuous controls
| ESCC-1800 |  | ESCC | 3600 |  | Constant Load (CL) | ESCC-1800 | 1.09 |  |  | Section III - Test Pump Efficiency of Bare Pump + Default Nominal Full Load Motor Efficiency + Default Part Load Loss Curve
| ESCC-3600 |  | ESFM | 1800 |  | Variable Load (VL) | ESCC-3600 | 1.09 |  |  | Section V - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor part Load Loss Curve
| ESFM-1800 |  | IL |  |  |  | ESFM-1800 | 1.1 |  |  | Section IV - Pump + Motor Tested Wire-to-Water Performance
| ESFM-3600 |  | RSV |  |  |  | ESFM-3600 | 1.09 |  |  | Section VII - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor/Control Part Load Loss Curve + Assumed Control Curve
| IL-1800 |  | ST |  |  |  | IL-1800 | 1.11 |  |  | Section VI - Pump + Motor + Control Tested Wire-to-Water Performance + Assumed Control Curve
| IL-3600 | [5 empty] | IL-3600 | 1.13
| RSV-1800 | [5 empty] | RSV-1800 | 1
| RSV-3600 | [5 empty] | RSV-3600 | 1
| ST-1800 | [5 empty] | ST-1800 | 1
| ST-3600 | [5 empty] | ST-3600 | 1.07
[6 empty] | N/A |  |  |  |  | DOE Equipment Category | C-value |  |  | Default Nominal Full Load Nominal Efficiency [ESCC, ESFM, IL, RSV & ST] |  |  | or horsepower/
[6 empty] | 1 | [5 empty] | Baseline | Standard |  | Motor Horsepower [MotorHP] | Efficiency (%) [ηmotor,full] |  | standard kilowatt equivalent
|  |  | 250 |  | 1 | 2 |  |  |  |  | ESCC-1800 | 134.43 | 128.47 |  |  | 1800 rpm | 3600 rpm |  | 2Pole | 4 Pole
|  |  | 200 |  | 1.5 | 3 |  |  |  |  | ESCC-3600 | 135.94 | 130.42 | "ESCC-250-1800":95.8, | ESCC-250-1800 | 95.8 | 95 | 1 | 77 | 85.5
|  |  | 150 |  | 2 | 4 |  |  |  |  | ESFM-1800 | 134.99 | 128.85 | "ESCC-200-1800":95.8, | ESCC-200-1800 | 95.8 | 95 | 1.5 | 84 | 86.5
|  |  | 125 |  | 3 | 6 |  |  |  |  | ESFM-3600 | 136.59 | 130.99 | "ESCC-150-1800":95.8, | ESCC-150-1800 | 95.8 | 94.1 | 2 | 85.5 | 86.5
|  |  | 100 |  | 5 | [5 empty] | IL-1800 | 135.92 | 129.3 | "ESCC-125-1800":95.4, | ESCC-125-1800 | 95.4 | 94.1 | 3 | 85.5 | 89.5
|  |  | 75 |  | 7.5 | [5 empty] | IL-3600 | 141.01 | 133.84 | "ESCC-100-1800":95.4, | ESCC-100-1800 | 95.4 | 93.6 | 5 | 86.5 | 89.5
|  |  | 60 |  | 10 | [5 empty] | RSV-1800 | 129.63 | 129.63 | "ESCC-75-1800":95, | ESCC-75-1800 | 95 | 93.6 | 7.5 | 88.5 | 91
|  |  | 50 |  | 15 | [5 empty] | RSV-3600 | 133.2 | 133.2 | "ESCC-60-1800":95, | ESCC-60-1800 | 95 | 93.6 | 10 | 89.5 | 91.7
|  |  | 40 |  | 20 | [5 empty] | ST-1800 | 138.78 | 138.78 | "ESCC-50-1800":94.5, | ESCC-50-1800 | 94.5 | 93 | 15 | 90.2 | 92.4
|  |  | 30 |  | 25 | Yes |  |  |  |  | ST-3600 | 138.78 | 134.85 | "ESCC-40-1800":94.1, | ESCC-40-1800 | 94.1 | 92.4 | 20 | 91 | 93
|  |  | 25 |  | 30 | No | [7 empty] | "ESCC-30-1800":93.6, | ESCC-30-1800 | 93.6 | 91.7 | 25 | 91.7 | 93.6
|  |  | 20 |  | 40 | N/A | [7 empty] | "ESCC-25-1800":93.6, | ESCC-25-1800 | 93.6 | 91.7 | 30 | 91.7 | 93.6
|  |  | 15 |  | 50 | [8 empty] | "ESCC-20-1800":93, | ESCC-20-1800 | 93 | 91 | 40 | 92.4 | 94.1
|  |  | 10 |  | 60 | [8 empty] | "ESCC-15-1800":92.4, | ESCC-15-1800 | 92.4 | 90.2 | 50 | 93 | 94.5
|  |  | 7.5 |  | 75 | [8 empty] | "ESCC-10-1800":91.7, | ESCC-10-1800 | 91.7 | 89.5 | 60 | 93.6 | 95
|  |  | 5 |  | 100 | [8 empty] | "ESCC-7.5-1800":91, | ESCC-7.5-1800 | 91 | 88.5 | 75 | 93.6 | 95
|  |  | 3 |  | 125 | [8 empty] | "ESCC-5-1800":89.5, | ESCC-5-1800 | 89.5 | 86.5 | 100 | 93.6 | 95.4
|  |  | 2 |  | 150 | [8 empty] | "ESCC-3-1800":89.5, | ESCC-3-1800 | 89.5 | 85.5 | 125 | 94.1 | 95.4
|  |  | 1.5 |  | 200 | [8 empty] | "ESCC-2-1800":86.5, | ESCC-2-1800 | 86.5 | 85.5 | 150 | 94.1 | 95.8
|  |  | 1 |  | 250 | [8 empty] | "ESCC-1.5-1800":86.5, | ESCC-1.5-1800 | 86.5 | 84 | 200 | 95 | 95.8
[14 empty] | "ESCC-1-1800":85.5, | ESCC-1-1800 | 85.5 | 77 | 250 | 95 | 95.8
[14 empty] | "ESCC-250-3600":95, | ESCC-250-3600 | 95
[14 empty] | "ESCC-200-3600":95, | ESCC-200-3600 | 95
[14 empty] | "ESCC-150-3600":94.1, | ESCC-150-3600 | 94.1
[14 empty] | "ESCC-125-3600":94.1, | ESCC-125-3600 | 94.1
[14 empty] | "ESCC-100-3600":93.6, | ESCC-100-3600 | 93.6
[14 empty] | "ESCC-75-3600":93.6, | ESCC-75-3600 | 93.6
[14 empty] | "ESCC-60-3600":93.6, | ESCC-60-3600 | 93.6
1.15 | [13 empty] | "ESCC-50-3600":93, | ESCC-50-3600 | 93
ST |  |  | Motor Rating | Coefficients for Motor & Control Part Load loss Factor Zi | [9 empty] | "ESCC-40-3600":92.4, | ESCC-40-3600 | 92.4
|  |  |  | a | b | c | [7 empty] | "ESCC-30-3600":91.7, | ESCC-30-3600 | 91.7
|  | 200 | MotorHP,NP > 50 | -0.8914 | 2.8846 | 0.2625 | MotorHP,NP ≤ 5 | -0.4658 | 1.4965 | 0.5303 |  |  |  | "ESCC-25-3600":91.7, | ESCC-25-3600 | 91.7
|  | 50 | MotorHP,NP > 20 and ≤ 50 | -1.5122 | 3.0777 | 0.1847 | MotorHP,NP > 5 and ≤ 20 | -1.3198 | 2.9551 | 0.1052 |  |  |  | "ESCC-20-3600":91, | ESCC-20-3600 | 91
yes |  | 20 | MotorHP,NP > 5 and ≤ 20 | -1.3198 | 2.9551 | 0.1052 | MotorHP,NP > 20 and ≤ 50 | -1.5122 | 3.0777 | 0.1847 |  |  |  | "ESCC-15-3600":90.2, | ESCC-15-3600 | 90.2
no |  | 5 | MotorHP,NP ≤ 5 | -0.4658 | 1.4965 | 0.5303 | MotorHP,NP > 50 | -0.8914 | 2.8846 | 0.2625 |  |  |  | "ESCC-10-3600":89.5, | ESCC-10-3600 | 89.5
[14 empty] | "ESCC-7.5-3600":88.5, | ESCC-7.5-3600 | 88.5
[14 empty] | "ESCC-5-3600":86.5, | ESCC-5-3600 | 86.5
[14 empty] | "ESCC-3-3600":85.5, | ESCC-3-3600 | 85.5
[14 empty] | "ESCC-2-3600":85.5, | ESCC-2-3600 | 85.5
[14 empty] | "ESCC-1.5-3600":84, | ESCC-1.5-3600 | 84
[14 empty] | "ESCC-1-3600":77, | ESCC-1-3600 | 77
|  |  | Section III to Section V - Rated Bare Pump + Regulated Extended Motor (Constant Load) | [10 empty] | "ESFM-250-1800":95.8, | ESFM-250-1800 | 95.8
|  |  | Section III to Section V to Section VII Bare Pump + regulated Extended Motor + Control (Variable Load) | [10 empty] | "ESFM-200-1800":95.8, | ESFM-200-1800 | 95.8
|  |  | Section III to VestionVII - Bare Pump + Extended Control (Variable Load) | [10 empty] | "ESFM-150-1800":95.8, | ESFM-150-1800 | 95.8
|  |  | Section V to VestionVII - Pump with regulated motor (calc) + Extended Control (Variable Load) | [10 empty] | "ESFM-125-1800":95.4, | ESFM-125-1800 | 95.4
|  |  | Section IV to VestionVII - Pump with regulated motor (test) + Extended Control (Variable Load) | [10 empty] | "ESFM-100-1800":95.4, | ESFM-100-1800 | 95.4
|  |  | Section IV to VestionVII - Pump with non-regulated motor (test) + Extended Control (Variable Load) | [10 empty] | "ESFM-75-1800":95, | ESFM-75-1800 | 95
[14 empty] | "ESFM-60-1800":95, | ESFM-60-1800 | 95
[14 empty] | "ESFM-50-1800":94.5, | ESFM-50-1800 | 94.5
[14 empty] | "ESFM-40-1800":94.1, | ESFM-40-1800 | 94.1
[14 empty] | "ESFM-30-1800":93.6, | ESFM-30-1800 | 93.6
[14 empty] | "ESFM-25-1800":93.6, | ESFM-25-1800 | 93.6
[14 empty] | "ESFM-20-1800":93, | ESFM-20-1800 | 93
[14 empty] | "ESFM-15-1800":92.4, | ESFM-15-1800 | 92.4
[14 empty] | "ESFM-10-1800":91.7, | ESFM-10-1800 | 91.7
[14 empty] | "ESFM-7.5-1800":91, | ESFM-7.5-1800 | 91
[14 empty] | "ESFM-5-1800":89.5, | ESFM-5-1800 | 89.5
[14 empty] | "ESFM-3-1800":89.5, | ESFM-3-1800 | 89.5
[14 empty] | "ESFM-2-1800":86.5, | ESFM-2-1800 | 86.5
[14 empty] | "ESFM-1.5-1800":86.5, | ESFM-1.5-1800 | 86.5
[14 empty] | "ESFM-1-1800":85.5, | ESFM-1-1800 | 85.5
[14 empty] | "ESFM-250-3600":95, | ESFM-250-3600 | 95
[14 empty] | "ESFM-200-3600":95, | ESFM-200-3600 | 95
[14 empty] | "ESFM-150-3600":94.1, | ESFM-150-3600 | 94.1
[14 empty] | "ESFM-125-3600":94.1, | ESFM-125-3600 | 94.1
[14 empty] | "ESFM-100-3600":93.6, | ESFM-100-3600 | 93.6
[14 empty] | "ESFM-75-3600":93.6, | ESFM-75-3600 | 93.6
[14 empty] | "ESFM-60-3600":93.6, | ESFM-60-3600 | 93.6
[14 empty] | "ESFM-50-3600":93, | ESFM-50-3600 | 93
[14 empty] | "ESFM-40-3600":92.4, | ESFM-40-3600 | 92.4
[14 empty] | "ESFM-30-3600":91.7, | ESFM-30-3600 | 91.7
[14 empty] | "ESFM-25-3600":91.7, | ESFM-25-3600 | 91.7
[14 empty] | "ESFM-20-3600":91, | ESFM-20-3600 | 91
[14 empty] | "ESFM-15-3600":90.2, | ESFM-15-3600 | 90.2
[14 empty] | "ESFM-10-3600":89.5, | ESFM-10-3600 | 89.5
[14 empty] | "ESFM-7.5-3600":88.5, | ESFM-7.5-3600 | 88.5
[14 empty] | "ESFM-5-3600":86.5, | ESFM-5-3600 | 86.5
[14 empty] | "ESFM-3-3600":85.5, | ESFM-3-3600 | 85.5
[14 empty] | "ESFM-2-3600":85.5, | ESFM-2-3600 | 85.5
[14 empty] | "ESFM-1.5-3600":84, | ESFM-1.5-3600 | 84
[14 empty] | "ESFM-1-3600":77, | ESFM-1-3600 | 77
[14 empty] | "IL-250-1800":95.8, | IL-250-1800 | 95.8
[14 empty] | "IL-200-1800":95.8, | IL-200-1800 | 95.8
[14 empty] | "IL-150-1800":95.8, | IL-150-1800 | 95.8
[14 empty] | "IL-125-1800":95.4, | IL-125-1800 | 95.4
[14 empty] | "IL-100-1800":95.4, | IL-100-1800 | 95.4
[14 empty] | "IL-75-1800":95, | IL-75-1800 | 95
[14 empty] | "IL-60-1800":95, | IL-60-1800 | 95
[14 empty] | "IL-50-1800":94.5, | IL-50-1800 | 94.5
[14 empty] | "IL-40-1800":94.1, | IL-40-1800 | 94.1
[14 empty] | "IL-30-1800":93.6, | IL-30-1800 | 93.6
[14 empty] | "IL-25-1800":93.6, | IL-25-1800 | 93.6
[14 empty] | "IL-20-1800":93, | IL-20-1800 | 93
[14 empty] | "IL-15-1800":92.4, | IL-15-1800 | 92.4
[14 empty] | "IL-10-1800":91.7, | IL-10-1800 | 91.7
[14 empty] | "IL-7.5-1800":91, | IL-7.5-1800 | 91
[14 empty] | "IL-5-1800":89.5, | IL-5-1800 | 89.5
[14 empty] | "IL-3-1800":89.5, | IL-3-1800 | 89.5
[14 empty] | "IL-2-1800":86.5, | IL-2-1800 | 86.5
[14 empty] | "IL-1.5-1800":86.5, | IL-1.5-1800 | 86.5
[14 empty] | "IL-1-1800":85.5, | IL-1-1800 | 85.5
[14 empty] | "IL-250-3600":95, | IL-250-3600 | 95
[14 empty] | "IL-200-3600":95, | IL-200-3600 | 95
[14 empty] | "IL-150-3600":94.1, | IL-150-3600 | 94.1
[14 empty] | "IL-125-3600":94.1, | IL-125-3600 | 94.1
[14 empty] | "IL-100-3600":93.6, | IL-100-3600 | 93.6
[14 empty] | "IL-75-3600":93.6, | IL-75-3600 | 93.6
[14 empty] | "IL-60-3600":93.6, | IL-60-3600 | 93.6
[14 empty] | "IL-50-3600":93, | IL-50-3600 | 93
[14 empty] | "IL-40-3600":92.4, | IL-40-3600 | 92.4
[14 empty] | "IL-30-3600":91.7, | IL-30-3600 | 91.7
[14 empty] | "IL-25-3600":91.7, | IL-25-3600 | 91.7
[14 empty] | "IL-20-3600":91, | IL-20-3600 | 91
[14 empty] | "IL-15-3600":90.2, | IL-15-3600 | 90.2
[14 empty] | "IL-10-3600":89.5, | IL-10-3600 | 89.5
[14 empty] | "IL-7.5-3600":88.5, | IL-7.5-3600 | 88.5
[14 empty] | "IL-5-3600":86.5, | IL-5-3600 | 86.5
[14 empty] | "IL-3-3600":85.5, | IL-3-3600 | 85.5
[14 empty] | "IL-2-3600":85.5, | IL-2-3600 | 85.5
[14 empty] | "IL-1.5-3600":84, | IL-1.5-3600 | 84
[14 empty] | "IL-1-3600":77, | IL-1-3600 | 77
[14 empty] | "RSV-250-1800":95.8, | RSV-250-1800 | 95.8
[14 empty] | "RSV-200-1800":95.8, | RSV-200-1800 | 95.8
[14 empty] | "RSV-150-1800":95.8, | RSV-150-1800 | 95.8
[14 empty] | "RSV-125-1800":95.4, | RSV-125-1800 | 95.4
[14 empty] | "RSV-100-1800":95.4, | RSV-100-1800 | 95.4
[14 empty] | "RSV-75-1800":95, | RSV-75-1800 | 95
[14 empty] | "RSV-60-1800":95, | RSV-60-1800 | 95
[14 empty] | "RSV-50-1800":94.5, | RSV-50-1800 | 94.5
[14 empty] | "RSV-40-1800":94.1, | RSV-40-1800 | 94.1
[14 empty] | "RSV-30-1800":93.6, | RSV-30-1800 | 93.6
[14 empty] | "RSV-25-1800":93.6, | RSV-25-1800 | 93.6
[14 empty] | "RSV-20-1800":93, | RSV-20-1800 | 93
[14 empty] | "RSV-15-1800":92.4, | RSV-15-1800 | 92.4
[14 empty] | "RSV-10-1800":91.7, | RSV-10-1800 | 91.7
[14 empty] | "RSV-7.5-1800":91, | RSV-7.5-1800 | 91
[14 empty] | "RSV-5-1800":89.5, | RSV-5-1800 | 89.5
[14 empty] | "RSV-3-1800":89.5, | RSV-3-1800 | 89.5
[14 empty] | "RSV-2-1800":86.5, | RSV-2-1800 | 86.5
[14 empty] | "RSV-1.5-1800":86.5, | RSV-1.5-1800 | 86.5
[14 empty] | "RSV-1-1800":85.5, | RSV-1-1800 | 85.5
[14 empty] | "RSV-250-3600":95, | RSV-250-3600 | 95
[14 empty] | "RSV-200-3600":95, | RSV-200-3600 | 95
[14 empty] | "RSV-150-3600":94.1, | RSV-150-3600 | 94.1
[14 empty] | "RSV-125-3600":94.1, | RSV-125-3600 | 94.1
[14 empty] | "RSV-100-3600":93.6, | RSV-100-3600 | 93.6
[14 empty] | "RSV-75-3600":93.6, | RSV-75-3600 | 93.6
[14 empty] | "RSV-60-3600":93.6, | RSV-60-3600 | 93.6
[14 empty] | "RSV-50-3600":93, | RSV-50-3600 | 93
[14 empty] | "RSV-40-3600":92.4, | RSV-40-3600 | 92.4
[14 empty] | "RSV-30-3600":91.7, | RSV-30-3600 | 91.7
[14 empty] | "RSV-25-3600":91.7, | RSV-25-3600 | 91.7
[14 empty] | "RSV-20-3600":91, | RSV-20-3600 | 91
[14 empty] | "RSV-15-3600":90.2, | RSV-15-3600 | 90.2
[14 empty] | "RSV-10-3600":89.5, | RSV-10-3600 | 89.5
[14 empty] | "RSV-7.5-3600":88.5, | RSV-7.5-3600 | 88.5
[14 empty] | "RSV-5-3600":86.5, | RSV-5-3600 | 86.5
[14 empty] | "RSV-3-3600":85.5, | RSV-3-3600 | 85.5
[14 empty] | "RSV-2-3600":85.5, | RSV-2-3600 | 85.5
[14 empty] | "RSV-1.5-3600":84, | RSV-1.5-3600 | 84
[14 empty] | "RSV-1-3600":77, | RSV-1-3600 | 77
[14 empty] | "ST-250-1800":86.5, | ST-250-1800 | 86.5
[14 empty] | "ST-200-1800":86.5, | ST-200-1800 | 86.5
[14 empty] | "ST-150-1800":85.5, | ST-150-1800 | 85.5
[14 empty] | "ST-125-1800":84, | ST-125-1800 | 84
[14 empty] | "ST-100-1800":84, | ST-100-1800 | 84
[14 empty] | "ST-75-1800":85.5, | ST-75-1800 | 85.5
[14 empty] | "ST-60-1800":84, | ST-60-1800 | 84
[14 empty] | "ST-50-1800":82.5, | ST-50-1800 | 82.5
[14 empty] | "ST-40-1800":81.5, | ST-40-1800 | 81.5
[14 empty] | "ST-30-1800":80, | ST-30-1800 | 80
[14 empty] | "ST-25-1800":78.5, | ST-25-1800 | 78.5
[14 empty] | "ST-20-1800":77, | ST-20-1800 | 77
[14 empty] | "ST-15-1800":75.5, | ST-15-1800 | 75.5
[14 empty] | "ST-10-1800":74, | ST-10-1800 | 74
[14 empty] | "ST-7.5-1800":74, | ST-7.5-1800 | 74
[14 empty] | "ST-5-1800":75.5, | ST-5-1800 | 75.5
[14 empty] | "ST-3-1800":75.5, | ST-3-1800 | 75.5
[14 empty] | "ST-2-1800":70, | ST-2-1800 | 70
[14 empty] | "ST-1.5-1800":70, | ST-1.5-1800 | 70
[14 empty] | "ST-1-1800":68, | ST-1-1800 | 68
[14 empty] | "ST-250-3600":86.5, | ST-250-3600 | 86.5
[14 empty] | "ST-200-3600":85.5, | ST-200-3600 | 85.5
[14 empty] | "ST-150-3600":84, | ST-150-3600 | 84
[14 empty] | "ST-125-3600":84, | ST-125-3600 | 84
[14 empty] | "ST-100-3600":81.5, | ST-100-3600 | 81.5
[14 empty] | "ST-75-3600":81.5, | ST-75-3600 | 81.5
[14 empty] | "ST-60-3600":81.5, | ST-60-3600 | 81.5
[14 empty] | "ST-50-3600":80, | ST-50-3600 | 80
[14 empty] | "ST-40-3600":78.5, | ST-40-3600 | 78.5
[14 empty] | "ST-30-3600":77, | ST-30-3600 | 77
[14 empty] | "ST-25-3600":74, | ST-25-3600 | 74
[14 empty] | "ST-20-3600":72, | ST-20-3600 | 72
[14 empty] | "ST-15-3600":72, | ST-15-3600 | 72
[14 empty] | "ST-10-3600":70, | ST-10-3600 | 70
[14 empty] | "ST-7.5-3600":68, | ST-7.5-3600 | 68
[14 empty] | "ST-5-3600":74, | ST-5-3600 | 74
[14 empty] | "ST-3-3600":70, | ST-3-3600 | 70
[14 empty] | "ST-2-3600":68, | ST-2-3600 | 68
[14 empty] | "ST-1.5-3600":66, | ST-1.5-3600 | 66
[14 empty] | "ST-1-3600":55, | ST-1-3600 | 55

## HI 40.5 database fields
All database entry fields should be able to imported from any one of the calculation method tabs (Section III, Section IV, Section V, Section VI or Section VII. Note Secondary Fields differ by Section
Initial Database Entry Fields for all Basic Model Listings-------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings------------------------------------------------Initial Database Entry Fields for all Basic Model Listings
[6 empty] | nsp |  | MotorHP or MotorHP,NP |  | Q100% | H100% | Q75% | H75% | Q110% | H110% |  | S |  | PEICL or PEIVL
Participant Company | Basic Model Designation | Rating Load Type | Configuration for which the pump is being rated | Test/PEI Calculation Method per Appendix A to Subpart Y of Part 431 | DOE Pump Category | Nominal Speed of rotation | DOE Equipment Category | Rated Motor Power used for default losses or Nameplate Rated Motor Power (MotorHP) | MotorHP and Speed | BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at BEP rate of flow at Nominal Speed of Rotation | Flow at 75% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 75% of BEP rate of flow at Nominal Speed of Rotation | Flow at 110% BEP rate of flow at Nominal Speed of Rotation (gpm) | Head (ft) at 110% BEP rate of flow at Nominal Speed of Rotation | Basic Model Full Impeller Diameter (in) | Number of Stages Tested | HI Approved Laboratory Registration Number | Enter PEI for Basic Model to be listed
xxxxx | xxx.xxx.xx | Constant Load (CL) | Bare Pump | Section V - Test Pump Efficiency of Bare Pump + Represented Nominal Full Load Motor Efficiency for Actual Motor Paired with Pump + Default Motor part Load Loass Curve | ST | 3600 | ST-3600 | 60 | 60-3600 | 349.83 | 424.43 | 262.37 | 498.89 | 384.81 | 383.48 | xxxxx | 9 | xxxx | 0.95
User enter - freeform entry | User Enter - Free form entered | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter - Dropdown menu | User Enter -Dropdown menu | User Enter - Dropdown menu | Calculation Combination of cells C & D | User dropdown | Calculation Combination of cells L & D | User enter - Freeform entry
| This is a unique designation for the product to be rated. Refer to 10 CFRxxxx |  |  | If CL is selected - Only sections III, IV and V are available If VL is selected - only section VI and VII are available | [13 empty] | Needs to communicate with HI PTLAP database to ensure it is a valid certificate number
Secondary Database Entry Fields based on initial fields entered
If Cell E4 is DOE Equipment Category - ST-3600 or ST-1800
If PEI Calculation Methods Section III |  |  |  | or | If PEI Calculation Methods Section IV or V |  |  |  | or | If PEI Calculation Methods Section VI or VII
P75%in,M | P100%in,M | P110%in,M |  |  | P75%in,M | P100%in,M | P110%in,M |  |  | P25%in,C | P50%in,C | P75%in,C | P110%in,C
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Bowl diameter (in) |  | Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Bowl diameter (in) |  | Control Input Power at 25% of BEP Rate of Flow (hp) | Control Input Power at 50% of BEP Rate of Flow (hp) | Control Input Power at 75% of BEP Rate of Flow (hp) | Control Input Power at 100% of BEP Rate of Flow (hp) | Bowl diameter (in)
35 | 40 | 45 | 4 |  | 35 | 40 | 45 | 4 |  | 2.5 | 10 | 18 | 40 | 4
User Enter - freeform entry |  |  | User Enter - Dropdown menu |  | User Enter - freeform entry |  |  | User Enter - Dropdown menu |  | User Enter - freeform entry |  |  |  | User Enter - Dropdown menu
OR
If Cell E4 DOE Equipment Category - ESCC-1800, ESCC-3600, ESFM-1800, ESFM-3600, IL-1800, IL-3600, RSV-1800 or RSV-3600
If PEI Calculation Methods Section III |  |  | or | If PEI Calculation Methods Section IV or V |  |  |  |  | or | If PEI Calculation Methods Section VI or VII
P75%in,M | P100%in,M | P110%in,M |  | P75%in,M | P100%in,M | P110%in,M |  |  |  | P25%in,C | P50%in,C | P75%in,C | P110%in,C
Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) |  | Driver Input Power at 75% of BEP Rate of Flow (hp) | Driver Input Power at 100% of BEP Rate of Flow (hp) | Driver Input Power at 110% of BEP Rate of Flow (hp) | Is motor regulated under 10 CFR 431.25 | If Yes - Nameplate nominal motor efficiency (%) |  | Control Input Power at 25% of BEP Rate of Flow (hp) | Control Input Power at 50% of BEP Rate of Flow (hp) | Control Input Power at 75% of BEP Rate of Flow (hp) | Control Input Power at 100% of BEP Rate of Flow (hp) | Is motor regulated under 10 CFR 431.25 | If Yes - Nameplate nominal motor efficiency (%)
35 | 40 | 45 |  | 35 | 40 | 45 | Yes | 95 |  | 2.5 | 10 | 18 | 40 | Yes | 95
User Enter - freeform entry |  |  |  | User Enter - freeform entry |  |  | User Enter - Dropdown menu | User Enter - freeform entry |  | User Enter - freeform entry |  |  |  | User Enter - Dropdown menu | User Enter - freeform entry
Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating--------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating----------------------------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating-----------------------------------------------------------------------------------------------------------Database Calculation Steps to get to HI Energy Rating
Ns | C | CBaseline |  | ηmotor,full | Lfull | ƞpump,STD | ƞpump,Baseline | Pu,100% | Pu,75% | Pu,110% | P100%STD | P75%STD | P110%STD | P100%Baseline | P75%Baseline | P110%Baseline | X100%STD | X75%STD | X110%STD | X100%Baseline | X75%Baseline | X110%Baseline | Y100%STD | Y75%STD | Y110%STD | Y100%Baseline | Y75%Baseline | Y110%Baseline | L100%STD | L75%STD | L110%STD | L100%Baseline | L75%Baseline | L110%Baseline | P100%in,STD | P75%in,STD | P110%in,STD | P100%in,Baseline | P75%in,Baseline | P110%in,Baseline | PERSTD | PERBaseline | PEIBaseline | ER
Calculate Specifc Speed | Lookup Standard C-Value | Lookup baseline C-Value | Pump type - MotorHP - Speed | Lookup default Motor efficiency | Standard (default) Full Load Motor Losses | Caculate Std pump Efficiency | Calculate baseline pump Efficiency | Calculate hydraulic power at 100% BEP | Calculate hydraulic power at 75% BEP | Calculate hydraulic power at 110% BEP | Calculate Standard Pump Power input at 100% BEP | Calculate Standard Pump Power input at 75% BEP | Calculate Standard Pump Power input at 110% BEP | Calculate Baseline Pump Power input at 100% BEP | Calculate Baseline Pump Power input at 75% BEP | Calculate Baseline Pump Power input at 110% BEP | Standard motor power ratio at 100% BEP | Standard motor power ratio at 75% BEP | Standard motor power ratio at 110% BEP | Baseline motor power ratio at 100% BEP | Baseline motor power ratio at 75% BEP | Baseline motor power ratio at 110% BEP | Standard Part Load Loss Factor at 100% BEP | Standard Part Load Loss Factor at 75% BEP | Standard Part Load Loss Factor at 110% BEP | Baseline Part Load Loss Factor at 100% BEP | Baseline Part Load Loss Factor at 75% BEP | Baseline Part Load Loss Factor at 110% BEP | Standard part load losses at 100% BEP | Standard part load losses at 75% BEP | Standard part load losses at 110% BEP | Baseline part load losses at 100% BEP | Baseline part load losses at 75% BEP | Baseline part load losses at 110% BEP | Standard Driver Power Input at 100% BEP | Standard Driver Power Input at 75% BEP | Standard Driver Power Input at 75% BEP | Baseline Driver Power Input at 100% BEP | Baseline Driver Power Input at 75% BEP | Baseline Driver Power Input at 75% BEP | Caclculate Pump Energy Rating Standard | Caclculate Pump Energy Rating Baseline | Calculate Pump Energy Index Baseline | Calculate HI Energy Rating
3741.6086 | 134.85 | 138.78 | ST-60-3600 | 81.5 | 13.6196 | 68.542 | 64.612 | 37.5324 | 33.0874 | 37.3021 | 54.7583 | 50.9748 | 55.2509 | 58.0889 | 54.0753 | 58.6115 | 0.91264 | 0.84958 | 0.92085 | 0.96815 | 0.90126 | 0.97686 | 0.93852 | 0.8941 | 0.94433 | 0.97769 | 0.93048 | 0.98381 | 12.7824 | 12.1773 | 12.8614 | 13.3158 | 12.6728 | 13.3991 | 67.5406 | 63.1521 | 68.1123 | 71.4047 | 66.7482 | 72.0106 | 66.2617 | 70.0475 | 1.0571 | 10.7134
calculation | Lookup | Lookup | Calculation Combination of cells C, L & D for later lookup | Lookup | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation | Calculation
#REF!